- Washington Utilities and Transportation Commission

- Intrastate Gas Distribution System

### Inspection Guide and Report

Puget Sound Energy

# UG-020639

##### Pipeline Company Name                                                                                Docket#

Roque Bamba

99

#### Pipeline Company Contact                                                                    Company ID#

805 156th Avenue NE

# 80

- Address								   Facility Insp. #

City

Bellevue, WA

(425) 462-3734

(425) 462-3770

Telephone				Fax

# Pipeline Inspection Facility (Unit):

King County, Georgetown District.

Name

6500 Ursula Avenue S

- Address

Seattle, WA

- City

- Telephone	  Fax

##### Operator Representatives

Name and Title

Rocky Bamba

WUTC Representatives

Joe Subists, Pipeline Safety Engineer

###### Name and Title

November 11, 2002 – November 22, 2002

Inspection Dates

February 14, 2001 – May 24, 2001

##### Date of Last Inspection

- Pipeline Facility History

Age (Range)

Early 1900s to present.

Size (Range)

½” to 20”.

Material Type

PE, Steel, Wrought Iron, Cast Iron, Copper.

Specifications

Various.

Miles of Main

See Annual Report – Not county specific. See Attachment 1.

Number of Services

See Annual Report – Not county specific. See Attachment 1.

Number of Leaks (Mains and Services)

3290.

Leaks Scheduled for Repair

571.

Gas Transportation Company

Williams.

# Reporting Requirements

1.	Does the operator submit an Annual Distribution report? (CFR 191.11 & WAC 480-93-200)

# Yes.

2.	Does the operator notify the WUTC by telephonic notice of a specified incident as required? (CFR 191.5 & WAC 480-93-183, 200 & 210)

##### Section 2.1.4 & 2.1.5.

3.	Are 30-day written reports following a specified incident sent to WUTC as required? (CFR 191.9 & WAC 480-93-183, & 200)

# Section 2.1.4 & 2.1.5.

4.         Has the Maximum Allowable Operating Pressure (MAOP) been established for the pipeline? (CFR 192.619, 192.621, 192.623 & WAC 480-93-183)

# Section 6.1.4, 6.1.5, 7.1.4.

5.         Procedures for Continuing Surveillance? (CFR 192.613)

Section 11.4.7.

a.	Has appropriate action been taken concerning changes in:

i.	class location?

# N/A – design to class 4.

ii.        failures?

# Ok. Report done. See Attachment 2 & 3.

iii.	leakage history?

# Have cast iron replacement program. Bare steel program in negotiation.

iv.	corrosion?

# Violations – brought upon database.

b.	Cathodic protection and other unusual conditions?

# Ok.

6.       	Procedures for Odorization? (CFR 192.625 & WAC 480-93-015)

# Section 4.8, 6.37, 7.2.2 & 7.2.3.

a.	Does the operator conduct periodic sampling?

# Ok.

b.	Is the gas odorized to 1/5 LEL?

# Ok.

7.	Procedures for Patrolling? (CFR 192.721)

# Section 11.4.

a.	Have patrolling areas been identified?

# Ok.

b.	Have mains located in business districts been patrolled at intervals not exceeding 4½ months but at least 4 times each calendar year where anticipated physical movement or external loading could cause failure or leakage?

# Ok.

c.	Have mains located outside business districts been patrolled at intervals not exceeding 7½ months but at least twice each calendar year where anticipated physical movement or external loading could cause failure or leakage?

# Ok.

8.	Have valves which might be required during an emergency been serviced at intervals not exceeding 15 months, but at least once each calendar year? (CFR 192.747)

# Valve 253 inspected late by one month. See attachment 4.

9.         Have vaults 200 cubic feet or more been inspected at interval not exceeding 15 months, but at least once each calendar year? (CFR 192.749)

# N/A.

a.	Does the inspection include repairing gas leaks, vents, and vault covers?

# Section 7.1.2.

10.       Procedures for Leakage Surveys? (CFR 192.723 & WAC 480-93-188)

# Section 11.2 & 11.3.

a.	Have business district areas been identified and defined?

# Ok.

b.	Have gas detector surveys been conducted in the business districts at intervals not exceeding 15 months, but at least once each calendar year? (CFR 192.723(b)(1))

# Ok.

- Have leakage surveys of the distribution system outside of the principal business areas been conducted as frequently as necessary, but at intervals not exceeding five years? (CFR 192.723(b(2))

# Leak survey required for Lake Washington Crossing. Infeasible to comply without a waiver.

d.        Have leakage surveys of cast iron, wrought iron, ductile iron, or non-cathodically protected steel pipe been conducted at intervals not exceeding eight months, but at least twice each calendar year? (WAC 480-93-188(e))

# Ok.

11.	Has the operator provided for calibration and maintenance of leak detection instruments? (WAC 480-93-188(2))

# Not checked.

12.       Procedures for Leak Repairs? (CFR 192.703 & WAC 480-93-18601)

# Section 7.6.

a.	Have leaks been appropriately classified Grade 1, Grade 2, or Grade 3?

# Ok.

b.	Have Grade 1 leaks been repaired or eliminated or continuous action taken as required?

# Ok.

c.	Have Grade 2 leaks been repaired or eliminated within 15 or 21 months?

# Ok.

d.	Have Grade 2 leaks been reevaluated at least once every 6 months?

# Ok.

e. Have Grade 3 leaks been reevaluated within 15 months? # Ok.

13.       Procedures for Inspecting and Testing Regulating Stations?  (CFR 192.739)

# Section 7.1.2.

a.	Have regulating stations been inspected at intervals not exceeding 15 months, but at least once each calendar year?

# Testing not done at regulator station 1084 because of lack of lock-up port. See Attachment 6. Also regulator station 35 required test frequency exceeded by 9 days.

b.	In good mechanical condition?

# Ok.

c.	Adequate from the standpoint of capacity and reliability of operation?

# Ok.

d.	Set to function at the correct pressure?

# Ok.

e.	Properly installed and protected from dirt, liquids or other conditions that might prevent proper operation?

# Ok.

14.       Procedures for Testing Relief Valves? (CFR 192.743)

# Section 7.1.2.

a.	Have relief devices (RV) been tested at intervals not exceeding 15 months, but at least once each calendar year?

# No, see question 13 (a).

b.       Does RV have sufficient capacity?

# Ok.

c.       Have RV been set at the proper set point?

# Ok.

15.       Tele-metering or Recording Gauges? (CFR 192.741)

# Section 7.1.3.

a.	Are any pipeline systems supplied by more than one district regulating station?

# Ok.

b.	Are tele-metering or recording gauges installed?

# Ok.

c.	Are there any indications of abnormally high or low pressure?

# Ok.

d.	Are unsatisfactory operating conditions being corrected?

# Ok.

16.       Procedures for line markers? (CFR 192.707, WAC 480-93-120 & 124)

# Section 6.36 & 7.4.3.

- Are line markers installed at class 1 & 2 locations?

# Ok.

b.	Are line markers installed at all bridge, railroad, irrigation and drainage ditch crossings?

# Ok.

- Do the line markers include the current name, telephone number, and the word Warning, Caution, or Danger?

# Ok. Still finding old markers but are changing as found.

17.       Does the operator have a written Damage Prevention program? (CFR 192.614, WAC 480-93-190 & RCW Title 19.122)

# Section 2.6 & 2.7.

a.	Member of a one-call system? If so provide I.D. number. (WAC 480-93-190 & 192.614)

# 154200.

b.	Does the operator have available a current list of Excavators? (192.614©(1))

# Ok.

c.	Provide notification concerning the program to the public and excavators? (192.614©(2))

# Ok.

d.	Provide means for receiving and recording notification of pending excavations? (192.614©(3))

# Ok.

e.	Provide for markings within two business days?

# Two companies are currently competing for contract.

f.	Provide for follow up inspections of the pipeline where there is reason to believe the pipeline could be damaged? (192.614©(6)

# Ok.

g. 	Provide for action to protect pipeline when an excavator is using drilling or boring equipment?

# Pot holes dug to get drill depth.

18.       Does the operator have a comprehensive public education program that includes customers, the public, appropriate government and excavators, that teaches them how to recognize and report a gas pipeline emergency? (CFR 192.616)

# Section 2.4 & 2.6.

a.	Does the program reach all areas in which the operator has pipeline facilities?

# Ok.

b.	Is the program conducted in English and other languages (commonly understood by a significant number and concentration of the non-English speaking population in the operator’s area)?

# N/A.

19.       Procedures for Abandonment and Inactivation of Facilities? (CFR 192.727)

# Section 6.17, 6.23 & 7.11.

a.	Disconnecting abandon pipe from the supply of gas?

# Section 6.23 (3).

i.	Purge the pipe of gas?

# Section 6.23 (3).

ii.	Seal all open ends?

# Section 6.23 (3).

b.	Lock or prevent the service valve from being opened on all discontinued services?

# Section 7.11 (2).

20.       Procedures for Purging the Pipeline? (CFR 192.629)

# Section 6.17.

- a.  	Provide for purging of the pipeline of air or gas?

# Section 6.17.

21.       Procedures for tapping pipelines under pressure? (CFR 192.627)

# Section 7.4.5.

- a.  	Provide training that qualifies personnel to perform hot taps?

# Section 7.4.5 (4).

22.       Procedures to prevent accidental ignition? (CFR 192.751)

# Section 7.9.

a.	Removal of ignition sources?

# Section 7.9 (2).

b.	Provide fire extinguisher?

Section 7.9 (3).

c.	Prevent welding or cutting on pipelines containing combustible mixtures?

# Section 7.9 (2).

d.	Post warning signs?

# Section 7.9 (2).

23.       Procedures for Failure Investigation? (CFR 192.617)

# Section 7.8.1.

a.  	Do the procedures established require analyzing accidents & failures, including laboratory analysis where appropriate, to determine the cause and to minimize a recurrence?

# Section 7.8.1 – No reference to laboratory analysis.

24.       Procedures & test requirements for re-instated or temporarily disconnected service lines? (CFR 192.725)

# Section 6.14 (b).

25.       Does the operator have a procedure to move or lower a gas pipeline? (WAC 480-93-175)

# Section 6.6.

26.       Procedures for testing all pipelines that will be installed by new construction, replacement, or repair? (CFR 192.503)

# Section 6.14.

Transmission Pipeline

27.       How does the operator patrol the pipeline R/W for factors that may affect safety and operation of the pipeline?  (CFR 192.705)

walk    drive     fly       other

a.	Does the operator follow up on problems noted?

# Ok.

b.	Are records adequate?

# Ok.

28.       Are maximum intervals between patrols in accordance with the table? (CFR 192.705)

# Section 11.4 (4) & (5).

29.       Are transmission line valves that might be required during an emergency inspected and partially operated once a calendar year not exceeding 15 months (CFR 192.745)

# See attachment 4.

30.       Procedures for leakage surveys of transmission lines available? (CFR 192.706 & WAC 480-93-188)

# Section 11.2.

31.       What types of leakage surveys are conducted?

# High occupancy structures facilities under wall to wall paving transmission lines, supply lines, cast & wrought iron, non cathodically protected pipe, protected with c.p., plastic pipe & special surveys.

32.       Have leak surveys been conducted at intervals not exceeding 15 months, but at least once each calendar year? (CFR 192.706)

# Ok.

33.       Does the operator have non-odorized natural gas transmission lines? (CFR 192.706)

# N/A.

a.  	Is the operator in compliance with WAC 480-93-015?

# Ok.

b.        Are leak surveys using a gas detector conducted in class 3 locations, at intervals not exceeding 7½ months, but at least twice each calendar year?

# Ok.

c.         Are leak surveys using a gas detector conducted in class 4 locations not exceeding 4½ months, but at least four times each calendar year?

# Ok.

Corrosion Control - Cathodic Protected Pipelines

34.	Are corrosion control procedures under the responsibility of a qualified person? (CFR 192.453)

# Section 10.3 (2).

35.	Which of the 5 criteria for cathodic protection in Appendix D does the operator use? (CFR 192.463)

# -0.85V, 100mv, net protective current.

36.	Does the selected criteria from Appendix D meet the requirements of this part? (CFR 192.463)

# Ok. –850 mv dc.

37.	Are buried pipelines cathodically protected? (CFR 192.455)

# Not all.

38.	Are buried pipelines electrically isolated from other underground structures? (CFR 192.467)

# Section 10.4.

39.	Are casings inspected for electrical shorts annually? (CFR 192.467 & WAC 480-93-115)

# Section 10.5 (4.4).

40.	Are casings that are in contact with the carrier pipeline surveyed within 90 days to determine if a hazardous condition exists? (CFR 192.467 & WAC 480-93-115)

# Section 10.5 (4.4).

- Are leak surveys conducted every 90 days?

# Section 10.5 (4.4).

41.	What measures are taken to mitigate corrosion of the encased pipeline when isolation is impractical? (CFR 192.467©)

# Section 10.4 (4.2).

42.	Are insulating devices kept from areas where a combustible atmosphere may be anticipated? (CFR 192.467(e))

# Section 10.4 (4.1).

43.       Protection provided to the pipelines against damage due to fault currents where pipelines are located in close proximity to electrical transmission tower footings? (CFR 192.467(f))

# Section 10.4 (4.3).

44.       Has each pipeline that is cathodically protected been tested at least once each calendar year, but with intervals not exceeding 15 months? (CFR 192.465(a))

# Ok.

45.	Has each cathodic protection rectifier been inspected at least six times each calendar year, but with intervals not exceeding 2½ months? (CFR 192.465(b))

# Ok.

46.       Are sufficient test stations available to insure adequate cathodic protection? (CFR 192.469)

# Section 10.2.

47.	Are there any separately protected or isolated pipelines less than 100 feet? (CFR 192.465)

# Section 10.5 (4).

48.	Are 10% of the separately protected or isolated lines monitored each calendar year with a different 10% checked each subsequent year, so that the entire system is tested in each 10-year period? (CFR 192.465)

# Ok.

49.	Are all exposed pipelines examined for evidence of corrosion and coating deterioration? (CFR 192.459)

# Section 10.7.

a. 	Does the company have procedures for examing cast iron for evidence of graphitization?

# Yes. Section 7.10

50.	Are records kept? (CFR 192.491©)

# Ok.

Corrosion Control - Non-cathodically Protected Pipelines

51.	Are effectively coated steel mains and service lines install before August 1, 1971 cathodically protected?  (CFR 192.457)

# Section 10.1.

52.	Does the operator have bare pipelines?

Yes.

    - Are they cathodically protected? (CFR 192.457(b))

# No.

b.	Are unprotected bare pipelines re-evaluated at intervals not exceeding 3 years? (CFR 192.465(e))

# Section 10.6.

53.	Have active corrosion leaks been found? (WAC 480-93-112)

# Yes.

a.	Does the operator investigate further to determine the extent of the corrosion? (WAC 480-93-112)

# Section 10.7.

b.	Is cathodic protection provided in areas of active corrosion? (CFR 192.457 & WAC 93-112)

# Section 10.6.

Internal Corrosion Control

54.	Is corrosive gas being transported by pipeline? (CFR 192.475)

# No.

55.	Whenever a pipe segment is removed from a pipeline, has it been examined for evidence of internal corrosion? (CFR 192.475(b))

# Section 10.7.

56.	Have coupons been utilized and checked two times each calendar year, but with intervals not exceeding 7 ½ months? (CFR 192.477)

# N/A.

Atmospheric Corrosion Control

57.	Have above ground facilities installed after 7/31/71, been cleaned and coated? (CFR 192.479)

# Section 6.11.

58.	Have above ground facilities, installed before 8/1/71, been investigated for corrosion and if it exists, are the facility cleaned and coated? (CFR 192.479)

# Section 6.11.

59.       Has the operator re-evaluated piping exposed to the atmosphere at intervals not to exceed 3 years for onshore piping and where necessary, taken remedial action? (CFR 192.481)

# Section 10.7.

Remedial Measures

60.	Does the operator have remedial action requirements? (CFR 192.483)

# Section 10.8.

61.	Are remedial actions taken within 90 days of discovering low PS reads? (WAC 480-93-110)

# Section 10.8.

62.	Does new and replacement steel pipe have a protective coating that meets the requirements of CFR 192.461?

# Section 10.1.

Corrosion Control Records

63.	Does the operator maintain records or maps showing the location of cathodically protected pipe and facilities for as long as the pipeline remains in service? (CFR 192.491)

# Section 10.1.

64.	Does the operator retain records of each test, survey, and inspections for at least 5 years? (CFR 192.491)

# Section 10.5.

- Joining Of Pipeline Materials (Welding)

65.	Does the operator have qualified written welding procedures? (CFR 192.225)

# Section 6.9.

66.	Does the operator have the destructive test results that qualify each procedure? (CFR 192.225)

# Section 13.4.

67.	Are the welders qualified in accordance with CFR 192.227 & 229?

# Section 13.4.

68.	Are welds inspected and tested in accordance with CFR 192.241?

Section 13.2.

Plastic Jointing

69.	Is plastic pipe used? (CFR 192.59)

# Yes.

70.	Manufacturer and type of plastic used?

# Not checked.

71.	What types of jointing are performed?

# Not checked.

72.	Written procedures established for jointing? (CFR 192.273)

# Not checked.

73.	Have procedures been qualified? (CFR 192.283)

# Ok.

74.	Have the individuals been qualified? (CFR 192.285)

# Section 13.6.

75.	Are the individuals qualified to inspect joints? (CFR 192.287)

# Section 13.6.

76.	Are all materials properly marked? (CFR 192.63)

# Section 3.1.

# Operation and Maintenance

77.	Does the Operating and Maintenance Plan include the following: (CFR 192.603, 605 & WAC 480-93-180)

# Ok.

a.  	Is the manual reviewed and updated at intervals not exceeding 15 months, but at least once each calendar year?

# Ok.

b.  	Instructions for employees covering O&M procedures during normal operations and repairs?

# Ok. Section 7.

c. 	Instructions for the repair of the pipeline?

# Section 7.6.

d.  	Instruction for controlling corrosion?

# Section 10.

e.  	Making construction records, maps and operating history available to appropriate operating personnel?

# Section 5.15.

f.  	Gathering of data needed for reporting incidents under part 191 and WAC rules in a timely and effective manner?

##### Section 2.1 & 2.3 of O&M Manual.

g.  	Starting up and shutting down any part of the pipeline in a manner designed to assure operation within the MAOP?

##### Section 7.42 of O&M Manual.

h.  	Periodically reviewing the work done by operator personnel to determine the effectiveness and adequacy of the procedures used in normal operation and maintenance and modifying the procedure when deficiencies are found?

# Section 1.4 of O&M Manual.

i.  	Are precautions in excavated trenches listed that will protect personnel from hazards of unsafe accumulation of gas?

##### Not checked.

78.	Are breathing apparatus, rescue harness, and lines available?

# Gas field procedure 0100.2040.

79.	Does the operator use pipe-type or bottle-type holders? (CFR 192.605(B)(10))

# N/A.

a.   	Provide for detecting external corrosion before the strength of the container has been impaired?

# N/A.

b.  	Periodic sampling and testing of gas in storage to determine the dew point of vapors contained in the stored gas which, if condensed, might cause internal corrosion or interfere with the safe operation of the storage plant?

# N/A.

c.   	Periodic inspection and testing of pressure limiting equipment to determine that it is in a safe operating condition and has adequate capacity?

# N/A.

80.	The following procedures were not found in the O&M plan:

##### N/A.

81.	Has the operator established procedures that require notification to customers that the operator does not maintain customer piping and is subject to potential hazards of corrosion and leaks? (CFR 192.16)

##### Section 2.10 of O&M Manual.

82.	Has the operator notified each customer (not later than August 14, 1996, or 90 days after the customer first receives gas at a particular location) of potential hazards as listed in the rule? (CFR 192.16)

# Section 2.10 of O&M Manual.

83.	Has the operator established procedures to require notification to customers that the installation of an excess flow valve is available to customers that have a new natural gas service line installed or a service line replaced, provided that the customer bears the cost of the installation?  (CFR 192.383)

##### Section 7.12 of O&M Manual.

a.	Does the excess flow valve meet the performance standards prescribed under Section CFR 192.381?

Not checked.

Emergency Plan

84.	Does the operator have a written emergency plan? (CFR 192.615)

# Ok.

85.	Does the plan include the following:

a.	Instructions for the handling of notices of events that require immediate response by the operator? (CFR 192.615(a))

# Section 3. Corporate Emergency Plan.

b.	Means of communicating with appropriate public officials regarding possible emergency? (CFR 192.615(a)(2))

# Section 3. Corporate Emergency Plan.

c.	Prompt response to each of the following emergencies: (CFR 192.615(a)(3))

i. 	Gas detected inside or near a building?

# Section 3. Corporate Emergency Plan.

ii.	Fire near a pipeline?

# Section 3. Corporate Emergency Plan.

iii. 	Explosion near a pipeline?

# Section 3. Corporate Emergency Plan.

iv.	Natural disaster?

# O&M Manual Section 7.5.1.

d.	Does the plan provide a description of the types of personnel, equipment, tools, & material that may be required at the scene of each type of emergency? (CFR 192.615(a)(4))

# Gas Field Procedures Section 0100.2090.

e.	Provisions directed towards protecting people first, then property? (CFR 192.615(a)(5))

# Section 3. Corporate Emergency Plan.

f.	How & where to perform emergency shutdown or pressure reductions? (CFR 192.615(a)(6))

# Emergency sectionalized Plan.

g.	Investigating & rendering safe any actual or potential hazard to life or property? (CFR 192.615(a)(7))

# Section 3. Corporate Emergency Plan.

h.	Does the investigator include procedures and action to protect life in the event that there are multiple leaks and migration of gas into nearby buildings? (66 FR 28027 5/21/01)

# Notice given to Rocky – will evaluate.

i.	Check for gas accumulation in nearby building?

# See above.

  - Take steps to promptly stop the flow of gas?

# Section 3. Corporate Emergency Plan.

i.	Directions for notifying additional public officials required at the emergency scene and coordinating activities with these officials? (CFR 192.615(a)(8))

# Section 3. Corporate Emergency Plan.

j.	Instructions for safely restoring service outages? (CFR 192.615(a)(9))

# Section 3. Corporate Emergency Plan.

k.	Provisions for investigating accidents and failures as soon after the emergency as possible? (CFR 192.615(a)(10))

# Section 7.8.1. Gas operation Standard.

86.	Has the operator made provisions for:

a.  	Furnishing applicable portion of the emergency plan to supervisory personnel who are responsible for emergency action? (CFR 192.615(b)(1))

# Goes to managers, first responders.

b.  	Training appropriate employees as to the requirements of the emergency plan? (CFR 192.615(b)(2))

# Section 3. Emergency Response Plan.

c.  	Reviewing activities following actual or simulated emergencies to determine if they were effective? (CFR 192.615(b)(3))

# Section 1. Emergency Response Plan.

d.  	Establishing mutual liaison with fire, police, & other public officials, such that each is aware of the other's resources and capabilities in dealing with gas emergencies? (CFR 192.615(c))

# Liaison assigned to each area – responsible for interacting with locals.