## Slide 1
Clark W Gellings, P.E. Fellow
Washington Utilities and Transportation Commission September 17, 2014
© 2014 Electric Power Research Institute, Inc. All rights reserved.

## Slide 2: Electric Power Research Institute
Together…Shaping the Future of Electricity
Notes: [May not need this slide depending on audience. If speaking to an audience not very familiar with EPRI, provides an opportunity to explain who we are and our mission.]
EPRI’s mission is to develop science and technology innovations that provide society with electricity that is safe, reliable, affordable and environmentally responsible.
The emergence of distributed energy resources is having, and will have, a significant impact on the power system. EPRI has initiated an integrated grid study to understand how DER technologies can be blended with existing resources and with evolving consumer choices to preserve the objectives of safe, reliable, affordable and environmentally responsible electricity delivery.
Now is the time to plan so the grid can fully realize the value of ALL resources, and also be responsive to customer needs. The integrated grid paper we released in February presents an action plan to transform to an integrated grid – an action that utilities, technology providers, policy makers and regulators can act upon so that together…we can shape the future of electricity

## Slide 3: Looking Forward
Notes: The Power System is Changing and this change is dominated by Distributed Energy Resources (DER), devices at the edge of the distribution system. Change is nothing new. Innovation has been changing the generation, delivery and use of electricity for over 130 years.
These changes are not planned or integrated with the electric power system. In many cases, the distribution system operators do not have visibility of how much electricity is generated or consumed within their networks.

## Slide 4: Distributed Energy Resources
Photo courtesy of NREL
Photovoltaics
Storage
Micro-generation
Fuel Cells
Plug-In Electric Vehicles

## Slide 5: How Might the Grid Evolve?
Grid Defection
Connected, but not Integrated
Partially Integrated
A Fully Integrated Grid
Where we are today
Policy, Regulation, Markets, Interconnection Rules and
Technology will Drive the Transformation of the Grid
Notes: How does it all fit together?
We’ve done a good job at connecting DER, but haven’t integrated it into the operation of the power system. Without the interconnection standards and the modifications to utility planning and integration across transmission and distribution systems, true integration will be difficult going forward, if not impossible.
Two ways that the grid can go from here. The path to the left (defection) is a popular topic for advocates and consumers alike, and is labeled by some as “Grid Defection” rather than integration. This produces a system which lacks the strength of an interconnected system, with customers subjected to the reduction in economy of scale and the difficulty of balancing a system on a smaller area, without the benefit of shared backup and pooled resources. Going the other way, there is no one-size-fits-all solution, with different stakeholders and systems able to coordinate to different levels. However, the goal is a fully integrated system, capable of making the best use of all connected resources.
One thing is crystal clear: the grid is going to change. Identifying a favorable end point that takes into account the capabilities, limitations, and concerns of all parties will deliver the most value to society. Collaboration and forethought are fundamental to this evolution, and we at EPRI look forward to being part of this journey.

## Slide 6: The Grid Provides Transactional Value
Notes: Perhaps the most important value that grid connectivity provides consumers, especially those with distributed generation, is the ability to install any size DER that can be connected to the grid. A utility connection enables consumers to transact energy with the utility grid, getting energy when the customer needs it and sending energy back to the grid when the customer is producing more than is needed. This benefit, in effect, shifts risks with respect to the size of the energy resource from the individual user to the party responsible for the resources and operation of the grid.
The figure above shows simulated results in which a customer offsets the total energy consumption for the day. However, only about 30% of the energy is “self-consumed” at the instant of consumption (as is consistent with a number of German studies which estimate self-consumption for an average consumer without storage to be 20-40%)

## Slide 7: Grid Delivers Balancing Resource Solar resource calendar for August 2012 shows irradiance profiles in NJ
Blue area: measured irradiance
Orange line: calculated clear sky irradiance
Notes: The grid serves as a reliable source of high-quality power in the event of disruptions to DER. This includes compensating for the variable output of PV and wind generation. In the case of PV, the variability is not only diurnal but also overcast conditions or fast-moving clouds can cause fluctuation of PV-produced electricity. The grid serves as a crucial balancing resource available for whatever period—from seconds to hours to days and seasons— to offset variable and uncertain output from distributed resources.
This slide is a report of irradiance profiles in NJ during August 2012. Very few daily profiles (in blue) match the calculated optimal (orange), and show significant variability due to cloud movements and other sources of shading.

## Slide 8: Grid Provides Reliability Service
Chart: 
| 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010
Series 1 | 142 | 130 | 138 | 136 | 142 | 149 | 157 | 152 | 159 | 142 | 149
System Average Interruption Duration Index (SAIDI) Without Major Events
Minutes
Year
Average Grid Reliability
99.97% excluding major events
Equivalent reliability services from local generation will require onsite redundancy
Notes: System Average Interruption Duration Index (SAIDI) is a metric that reflects the number of minutes per year that an average customer would experience a power outage, excluding major events (such as hurricanes, blizzards, etc). A national average SAIDI of 140 minutes indicates a 99.97% reliability excluding those major events.
Reference: "IEEE Distribution Reliability Benchmarking 2011 Results," IEEE Distribution Reliability Working Group, 2013.

## Slide 9: The Grid Provides Startup Power
Notes: The grid provides instantaneous power for appliances and devices such as compressors, air conditioners, transformers and welders that require a strong flow of current (“in-rush” current) when starting up. This enables them to start reliably without severe voltage fluctuation. Without grid connectivity or other supporting technologies, a conventional central air conditioning compressor relying only on a PV system may not start at all unless the PV system is oversized to handle the in-rush current.
The figure illustrates the instantaneous power required to start a residential air conditioner. The peak current measured during this interval is six to eight times the standard operating current. While the customer’s PV array could satisfy the real power requirements (but not the reactive) of the heating, ventilating and air conditioning (HVAC) unit during normal operation, the customer’s grid connection supplies the majority of the required starting power.

## Slide 10: Grid Connectivity Reduces Harmonic Impact
Notes: The grid’s high fault current level also results in higher quality voltage by limiting harmonic distortion and regulating frequency in a very tight band, which is required for the operation of sensitive equipment. Similarly, the inherent inertia of a large, connected system minimizes the impact of disturbances, such as the loss of a large generators or transmission lines, on the system frequency. As shown in the figure, grid-connected consumers on average will experience voltage that closely approximates a sinusoidal waveform with very little harmonic distortion.
In contrast, voltage from a distributed system that is not connected to the grid will generally have a higher voltage harmonic distortion, which can result in malfunction of sensitive consumer end-use devices. Harmonics cause heating in many components, affecting dielectric strength and reducing the life of equipment, such as appliances, motors, or air conditioners. Harmonics also contribute to losses that reduce system efficiency. In addition, a disturbance occurring inside the unconnected system will create larger deviations in frequency than if the system maintained its connection to the larger grid.

## Slide 11: U.S. Average Cost to Consumers
Notes: This slide shows that, based on the U.S. Department of Energy’s Annual Energy Outlook 2012, an average customer consumes 982 kWh per month, paying an average bill of $110 per month, with the average cost of $70 for generation of electricity. That leaves $30 for the distribution system and $10 for the transmission system -- known together as “T&D”. These are average values, and costs vary among and within utilities and across different types of customers and in different type of market structures.
Most costs associated with T&D are related to capacity (except for a small fraction representing system losses – estimated to be $3 per month per customer from recent studies in California).
Working with recent data from PJM regarding the cost of energy, capacity, and ancillary services it is possible to estimate that 80% of the cost of generation is energy related, leaving the rest for capacity and grid services. This 80-20 split will depend on the market and in the case of a vertically integrated utility will depend on the characteristics of the generation assets and load profile, but it is a useful average figure.
The combination of transmission, distribution and the portion of generation that provides supply capacity averages $51/month while energy costs average $59/month. These costs vary widely across the United States and among consumers, and also will vary with changes in generation profile and the deployment of new technologies such as energy storage, demand response-supplied capacity

## Slide 12: Cost Projection for Off-Grid Local Energy Resource
Oversized PV Array
Additional Electronics
Multi-day Storage
Backup Generation
Controlled Load
1 Does not include additional cost of energy from local resources
Photo courtesy of NREL
Monthly Cost to Provide Grid Services from Local Resources1
Projected Cost in 2020
Photo courtesy of NREL
$228-$361
$165-$262
Notes: Cost figures reflect the additional cost to take a residence that produces 100% of its energy locally (from PV) and turn it into a self-sufficient entity that can operate without a grid connection.
These costs include:
-Extra PV Panels (beyond the annual kWh requirement)
-Battery Storage
-Charge Controller
-Backup Generator
Which are then amortized across the lifetime of the project (20 years)
Software Package: HOMER Energy
Location: St. Louis, MO and San Francisco, CA
Analysis includes appropriate incentives Federal ITC and net-energy-metering
Load profile provided by OpenEI for St. Louis metro area (12MWh/yr) and San Francisco, CA (7.67MWh/yr)
Real interest rate of 3.5% (Nominal 5.5% APR – 2% inflation)
PV System (Array + Inverter) Installed Cost: $3-$4/W installed (after incentive)
  GoSolarCalifornia – 2012 Averages
PV System DC-AC derating of 80% (based on fixed-tilt system)
Battery Cost: $300-$400/Useable kWh Capacity (Representative Retail Pricing – EPRI Staff)
System Controller: $600/kW (Representative Retail Pricing)
System O&M: Includes $32/kW/yr PV system O&M + $0.50/hr Generator O&M + $3/battery/yr
20 year lifetime of project (no salvage)
2020 Estimates:
PV Installed Costs: $1.50-$2/W Installed (Sunshot Target)
Battery Cost: $200-$300/Useable kWh Capacity (EPRI Staff Estimate)

## Slide 13: CAISO Net Load – 2012 Through 2020
Source: California ISO
27,000
25,000
23,000
21,000
19,000
17,000
15,000
13,000
11,000
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
2012
2013
2014
2015
2016
2017
2018
2019
2020
Typical March day – significant change starting in 2015
Potential over-generation

## Slide 14: The “Duck” Curve is for Real
Source: ENEL – Measured Data from Southern Italy and CAISO analysis
Increased requirement for downward ramping capability in the morning
More upward ramping capability is required when sun goes down
Need lower minimum generation levels to avoid over-generation
Not Just Resource Adequacy but the Adequacy of Resource of the Right Type

## Slide 15
Source: Amprion GmbH
max. PV : 23.952MW approx. 72% of inst. capacity (21.07.2013, 14:00)
MW PDE
Chart: h
Solar Energy: Installed Capacity and Production (2013)
h-Values for 2013

## Slide 16
RES: Installed Capacity and Production
h-values since 2011
MW PDE
max. RE*: 35.768MW
wind: 16.698MW
PV: 19.070MW approx. 56% (18.04.2013)
min. RE*: 148MW wind: 148MW PV: 0MW approx. 0,2% (17.02.2013)
h-Values since 2011
Renewable Energy
Installed Capacity
yearly average
Source: Amprion GmbH

## Slide 17
Wind and Solar Infeed vs. Load in Germany
Time: Sunday, 17 October 2013 (day with lowset renewable infeed)
Sources: * EEG/KWK-G ** EEX-Transparenzplattform *** ENTSO-E
h-values
17 Februar 2013 , 04:00 h
Load approx. 41.300MW
Wind+PV-Infeed approx. 150MW
MW
 only 0,4% of load covered by renewables
*
*
*
**

## Slide 18
Wind and Solar Infeed vs. Load in Germany
Time: Thursday, 03 October 2013 (public holiday)
03 Oktober 2013 , 14:00 h
Load approx. 51.407MW
Wind+PV-Infeed approx. 34.235MW
 67% of load covered by renewables
Datenquellen: * EEG/KWK-G ** EEX-Transparenzplattform *** ENTSO-E
h-values
MW
*
*
*
**

## Slide 19: Why Interconnection Guidelines Needed Risk of Wide-Spread PV Disconnection
50.8
50.6
50.4
50.2
50.0
49.8
49.6
49.4
49.2
Grid Frequency in Hz
Time in Seconds
0 10 20 30 40 50 60
Source: T. K. Vrana (2011)
Previous Interconnection Rules
German Operating Frequency Limit
Germany
As of 2012 PV Inverters were not required to provide frequency support and disconnect from the grid if the frequency reaches 50.2 Hz
This is similar to all current interconnection requirements in US as per IEEE 1547-2003
Notes: The plot above shows simulation results of German system frequency with a significant percentage of generation capacity as inverter-based DER with existing connection rules. The original rules forced inverters to “trip” offline if the system frequency reaches 50.2Hz. This issue raised significant stability concerns for the German system.
As a result, Germany is requiring that all existing inverters with a capacity greater than 3.68 kVA be retrofitted to include frequency control. The cost of the retrofit is estimated to be $300 million.
Experience in Germany provide a useful case study regarding the potential consequences of adding extensive amounts of DER without appropriate collaboration, planning and strategic development.

## Slide 20: Germany: Higher Penetration of Local Generation Necessitates an Integrated Approach
Installed Capacity (2013)
Solar
Wind
Interconnection Rules
Grid frequency support
Grid Infrastructure Upgrade
~$27.5B-$42.5B upgrade
Two Way Communication
Enabled by Advanced Distribution Management
~63GW of Installed Wind and PV – mostly connected to LV and MV grid
Source: Fraunhofer Institute, Germany
Recent Changes in Germany to Address Concern of Grid Reliability

## Slide 21: The Integrated Approach
Community LEN1
Campus LEN
Building LEN
Bulk Power System
Local Resources are Also Part of Grid Operation and Planning
1LEN: Local Energy Network
Distribution System
Master Controller
Distribution Management System
Master Controller
Master Controller
Market Operator
System Operator
Notes: Today’s grid is integrated electrically from central generation to consumers but optimization of generation resources is primary done on the bulk power system using the transmission grid – in an integrated approach the distribution grid is strengthened (re-conductoring) to enable higher penetration of local generation and modernized to operate more as a transmission grid to optimize local generation resources with central generation resources to provide the reliability and quality of power to consumers
An integrated grid overall will provide the lowest cost to consumers than any of the alternative: 1. Today

## Slide 22: Interconnected but Not Integrated
Interconnected Value of Grid Connectivity
Integrated Value of DER and Grid
Integration Enables Values of all Resources
Voltage
Quality
Efficiency
Energy
Transaction
Reliability
Startup
Power

## Slide 23: DER Penetration Feeder Hosting Capacity: A Brief Primer
Baseline – No PV
PV Penetration 1
PV Penetration 2
PV Penetration 3
Beyond…
Increase Penetration Levels Until Violations Occur
voltage
protection
power quality
thermal
PV Systems
Process is repeated 100’s of times to capture many possible scenarios
Notes: 1 minute
Key Message:
Remind them they have seen this the day before during the IG Next Phase Presentation
Quickly go over the process one more time as a recap and briefly say how we have made DSS a tool for the industry and for the academia and all researchers
Transition to Next Slide
Let’s take a real example of how this method can be used to assess a feeder- this is also most likely a repeat of Day 1

## Slide 24: DER Penetration Hosting Capacity: Sample Results
2500 cases shown Each point = highest primary voltage
ANSI voltage limit
Maximum Feeder Voltages (pu)
Increasing penetration (kW)
Minimum Hosting Capacity
Maximum Hosting Capacity
Total PV: 540 kW
Total PV: 1173 kW
Voltage violation
No observable violations regardless of size/location
Possible violations based upon size/location
Observable violations occur regardless of size/location
Notes: 1 minute
Key Message:
Here is how sausage is made
key simplicity even though under the hood it is a complex process –
key visualization
Why do they care: this is a consistent, repeatable and a transparent process that anybody can use and you can compare apples to apples – our Next Phase IG framework will be build upon this foundation
Transition to Slide 2
Once you have the assessment for one feeder you can do it for all your feeders

## Slide 25: Power System Impact Understanding System Impacts of DER
Localized Voltage & Capacity in Long Circuits
Prevalent voltage, Capacity & Protection Issues
Reverse Power Flow Reactive Power Balance
Voltage & Frequency Stability
Increasing Re-dispatch Transmission Constraint
Increasing Penetration Level
Customer
Distribution
Substation
Sub-transmission
Transmission
Central Generation
Generation Capacity & Ancillary Service
Voltage Support
Loss Reduction
T&D Avoided Capacity
Loss Reduction
Frequency Support
Energy, Capacity & Ancillary
Increasing Penetration Level

## Slide 26: Foundation of An Integrated Grid
Grid Modernization
Communication Standards and Interconnection Rules
Integrated Planning and Operations
Informed Policy and Regulation
Notes: Grid Modernization – Modernizing the grid will include re-conductoring in parts of the distribution system where higher level of penetration is expected and augmenting its infrastructure along with deploying technologies such as distribution management systems (DMS), communication, sensors, and energy storage. “Grid” in the context of an integrated grid includes technologies that are not just on the T&D side but also could be on the customer side. It is anticipated that this combination of infrastructure reinforcement and smart technology deployment can yield the lowest-cost solution for a given penetration level of DG in a feeder.
For these technologies to effectively work together we need a national imperative to standardize the way these technologies along with the DER will talk with each other and how the interconnection rules will enable this coordinated central and distributed resource integration. Germany, after learning the lesson from the past decade, has already done that by changing interconnection rules from Jan 2013.
Even if we have technologies and the communication standard and the interconnection rule – we still will need to ensure that during the planning and operation we have rules of engagement between a DER owner or aggregator and DSO and then with a DSO and a TSO or ISO. This will become a challenge in areas where all these functions are done separately but without integrated planning and operation we will NOT be able to realize the benefit of the increasing penetration of DER and ultimately the customers will pay with lower reliability and higher cost of integration . There are serious technical questions that needs to be addressed and agreed upon – what information and data is needed from DER to DSO from DSO to TSO/ISO – what is the speed of this data transfer? How reliable this communication needs to be? How do we ensure cyber security for this ubiquitous communication? These are some of the challenges that EPRI will be addressing in the next phase – not alone and not just working with the utilities – but working with you and the technology providers and the system operators
And finally after having all these we will still not be able to transform to an integrated grid unless we have updated our market and rate structures to ensure that we are valuing both capacity and energy and we are valuing all resources that contributes to capacity and energy and we have clear technical guidelines on the performance metrics that is needed to contribute to energy and resources and all customers are equitably paying for these

## Slide 27: Action Plan
Inform Stakeholders on Key Concept & Challenges
Benefit/Cost Framework for Different Designs
Global
Demonstrations
Data, Information
and Tools
Global Collaboration to Establish the Science, Engineering and Economics
Notes: The need for credible, fact based data and information for all stakeholders to ensure the foundation for developing integrated grid is anchored in science and economics AND the need for a collaborative approach
The different stakeholders - Policy makers, regulators, standards and research and technology providers and then utilities or broadly Retail/DSO/TSO/ISO. Given the diverse technical approaches possible for a given distribution feeder and specific levels of DER integration, a collaborative approach is essential in developing the comprehensive knowledge repository of costs, benefits, performance and operational requirements.
The framework for assessing the cost, benefit and performance of the different approaches that will work for different types of power systems to transform to an interred grid - this is the design of experiments. Identify technology combinations that will lead to cost effective investment to modernize the grid while supporting the technical basis for DER interconnection requirements.
A global demonstration or experiments that uses the framework - the results of the experiments provides the knowledge and information and science based data and tools that are used by the industry to realize the transformations that are needed. No one entity has the resources to conduct the demonstrations and the associated engineering analysis to document costs, benefits, and performance of all technology options across all types of distribution feeders. EPRI proposes using its collaborative approach globally to develop a comprehensive repository of data and information that can be used to move toward the Integrated Grid
Need to make the case that all who are involved in the transformation by advancing the FOUR key platforms will need a comprehensive and a consistent set of data and tools and information that enables making the decision of what technologies are the most cost effective and in what systems
Data is needed from DER to DSO to TSO or vice versa.

## Slide 28: Action Plan 3 Key Areas & Research Challenges
Benefit - Cost Framework
Interconnection Technical Guidelines
Grid Planning & Operations
Collaboration with All Stakeholders

## Slide 29: Overall Benefit Cost What is Included & What is Not
Customer Perspective
Utility- Cost Function
Utility Operations (people and how they do their jobs: non-fuel O&M, non-production assets, safety)
System Operations (the power system and its efficiency: losses, combustion, dispatch optimization, emissions)
Utility Assets (production assets required: GT&D)
Reliability & Power Quality (frequency and duration of customer interruptions, harmonics, sags/swells, voltage violations)
Customer (equipment & other direct customer costs)
Society (jobs, security, environmental and other economic costs and benefits
Included EPRI’s Methodology based on Power System Analysis and Economics
Not in scope of EPRI’s Methodology

## Slide 30: Building Upon Prior Efforts
Many have contributed to specific aspects of the framework
Need comprehensive approach: connecting all puzzle pieces
Notes: There is a significant amount of available research and previous studies that will be leveraged during Phase II. Determination of transmission and distribution expansion needs based on expected photovoltaic (PV) deployment have been reported by Southern California Edison (SCE) in 2012 and are continuing under the California Solar Initiative (CSI) Round IV [1]. Classification of distribution enhancement options have been presented by both the European Union’s PV GRID initiative [2] and DERlab consortium [3]. “Value of Solar” studies by SAIC [4], Xcel Energy [5], Clean Power Research (CPR ) [6], and others provide example approaches for itemizing the costs and benefits associated with DER and classifying the value streams by stakeholder and monetization strategy. EPRI, as part of Department of Energy (DOE) funded efforts, has developed a cost-benefit framework for smart grid investments that will aid in investment categorization and stakeholder identification [7]. As the value streams are consolidated, the impact of cost allocation and recovery on utility customer classes has been studied extensively by Energy and Environmental Economics, Inc. (E3) for both California [8] and Hawaii [9]. Also recent efforts in Austin Energy and Minnesota are other examples to address DER.
HOWEVER – each of these addresses pieces of the pie BUT NOT the entire pie.

## Slide 31: Interconnection Guidelines New Technical Considerations
Future Interconnection Standards Should Consider
  Voltage Support
  Frequency Support
  Fault Ride-Through
  DER/DSO Communication
EPRI working on recommended technical guidelines for voltage and frequency ride through capability for DG based on new IEEE 1547a
Notes: Both for planning and operation – what information is needed, who communicated what with whom. We have done this in the EMS world on the transmission side – we need to do this for the distribution system as well.
Two examples:
Imagine you have a distribution system with a feeder where you expect in future years to exceed the substation rating during a summer peak. You have the option to change the transformer or to install strategically placed storage near customer PV, which can defer the upgrade to a later date. How can you do this unless DER is part of the planning process?
Also imagine in a feeder you have significant penetration of PV and during a bright summer day you need to curtail the PV to ensure that feeder rating is not violated. Otherwise you may need to change the whole feeder and re-conductor the entire system. How do you do this without operationally integrating DER with the system?
While these two examples illustrate how DER can help in alleviating some of the need for grid augmentation but for widespread penetration grid HAVE to be augmented – an integrated grid allows this augmentation to be cost effective since in some cases DER can help in delaying or not requiring augmentation

## Slide 32: Grid Planning and Operation Transmission/Distribution Interface Needed
Transmission/ Independent System Operator (TSO/ISO)
Distribution System Operator (DSO)
Distributed Energy Resource (DER)
Establish technical requirements for transmission-distribution interface in a DER future
  Scheduling
  Real-time balancing
  Integrated markets
  Planning
  T&D operation
  Integrated System Modeling
Requires a coordinated effort among all stakeholders
Notes: Both for planning and operation – what information is needed, who communicated what with whom. We have done this in the EMS world on the transmission side – we need to do this for the distribution system as well.
Two examples:
Imagine you have a distribution system with a feeder where you expect in future years to exceed the substation rating during a summer peak. You have the option to change the transformer or to install strategically placed storage near customer PV, which can defer the upgrade to a later date. How can you do this unless DER is part of the planning process?
Also imagine in a feeder you have significant penetration of PV and during a bright summer day you need to curtail the PV to ensure that feeder rating is not violated. Otherwise you may need to change the whole feeder and re-conductor the entire system. How do you do this without operationally integrating DER with the system?
While these two examples illustrate how DER can help in alleviating some of the need for grid augmentation but for widespread penetration grid HAVE to be augmented – an integrated grid allows this augmentation to be cost effective since in some cases DER can help in delaying or not requiring augmentation

## Slide 33: Global Demonstrations & Modeling Preparing for Two Types of Demonstrations
Methodology Demonstration: System wide application of the Phase II methodology for a particular power system to assess the feasibility of an integrated benefit/cost methodology
Technology Demonstration: One or more combination of technology demonstration for a specific part of a power system to assess the performance and benefit/cost of the technology

## Slide 34: Together…Shaping the Future of Electricity
www.EPRI.com/integratedgrid
Download Your Copy of the Paper
For Additional Information Contact:
Barbara Tyran at btyran@epri.com
Karen Forsten at kforsten@epri.com