## Staff Analysis of Attachment 1
Cascade Natural Gas Corporation
Staff Analysis on Attachment 1 extracted from company's Maximum Allowable Operating Pressure Determination & Validation Plan filed in docket UG-150120
| Filename: 150120-CNG-Cply-Rpt-PLAN-ADD-SEGMENTS-12-29-17.pdf | [28 empty] | Staff's work shown in italics; summary begins in cell AC3229
Data as originally extracted
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year | Total segment count | Staff: is this segment pre-code (0) or post-code (1) | Pre-Code footaage | Post-code footage | Is this segment icompliant (valid?) yes-1 , no -blank | Valid pre-code footage | Valid post-code footage | Valid Pre-code segments | Valid Post-code segments
50202-T | 009-V-045, 046, 051, 053 | 499 | 3 |  | 418 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 47.69% | 47.69% | 1996 | 193 | 143.19 | Pressure Test/Replace | 2018-2019 | 1 | 1 | 0 | 193 |  | 0 | 0
20C6308 | 8" Kitsap Line | 366 | 3 |  | 802 | 750 | 535 | 250 |  | 250 |  | NA | UNVALID | 8.625 | 0.188 | 46000 | 0.8 | NO | NO | YES | 18.25% | 18.25% | 1963 | 18760.2 | 86.25 | 116 Segment, Expose/Verify | 2016 | 1 | 0 | 18760.2 | 0 |  | 0 | 0
50202 | 009-V-043, 044, 047, 048, 049, 050 | 499 | 3 |  | 376 | 750 | 500 | UNKV |  | 376 |  |  | UNVALID | 12.75 | 0.25 | 24000 | 0.8 | YES | YES | YES | 53.02% | 53.02% | 1996 | 62.9 | 117.52 | In-Situ Test | 2018-2019 | 1 | 1 | 0 | 62.9 |  | 0 | 0
44000-T | 8" Kitsap Line (Shomocker Creek, 009-V-045) | 499 | 3 |  | 418 | 1080 | 720 | UNKV |  | 418 |  | X | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 47.69% | 16.03% | 1995 | 15.2 | 112.69 | 116 Segment, Expose/Verify | 2017 | 1 | 1 | 0 | 15.2 |  | 0 | 0
20C6308 (R-11) | 009-R-011 | 809 | 3 |  | 1373 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 8.625 | 0.322 | 46000 | 0.8 | NO | NA | NA | 23.55% | NA | 1964 | 24.2 | 108.05 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 24.2 | 0 |  | 0 | 0
77C6321 | 4" Montesano H.P. Distribution System | 135 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 8.11% | NA | 1964 | 1763.7 | 85.11 | 116 Segment, Replace | 2023 | 1 | 0 | 1763.7 | 0 |  | 0 | 0
75C6817 | 009-R-001 | 305 | 3 |  | 1183 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.28 | 35000 | 0.8 | NO | NO | YES | 10.31% | 10.31% | 1964 | 25 | 82.31 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 25 | 0 |  | 0 | 0
75C6312 | 009-V-009, 015, 037, 038 | 150 | 3 |  | 499 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 8.625 | 0.322 | 35000 | 0.8 | NO | YES | YES | 9.01% | 9.01% | 1965 | 62.5 | 77.51 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 62.5 | 0 |  | 0 | 0
20C6308 (R-12) | Inlet 009-R-012 | 366 | 3 |  | 1106 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NA | NA | 9.93% | NA | 1964 | 27.5 | 75.43 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 27.5 | 0 |  | 0 | 0
41639 | Inlet 009-R-035 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 1992 | 31.1 | 71.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 31.1 |  | 0 | 0
44000 | 12" Kitsap H.P. Line | 499 | 3 |  | 1017 | 1080 | 720 | 250 |  | 250 |  | X | UNVALID | 12.75 | 0.312 | 52000 | 0.8 | NO | NO | YES | 19.61% | 16.31% | 1995 | 35827.6 | 70.61 | 116 Segment, Expose/Verify | 2017 | 1 | 1 | 0 | 35827.6 |  | 0 | 0
22551 | Inlet 009-R-022 | 155 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 9.31% | NA | 1973 | 2.8 | 70.31 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 2.8 |  | 0 | 0
78C7902 | 2" Elma Rendering Plant H.P. Line | 150 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | YES | YES | 3.30% | 4.82% | 1964 | 5906 | 69.32 | 116 Segment, Replace | 2022 | 1 | 0 | 5906 | 0 |  | 0 | 0
1265 | Inlet M&R CC000112 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 2001 | 82.7 | 67.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 82.7 |  | 0 | 0
50200 (V-54) | 009-V-054 | 499 | 3 |  | 1223 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NA | NA | 16.31% | NA | 1997 | 30.6 | 66.31 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 30.6 |  | 0 | 0
18828 | Inlet 009-R-032 | 499 | 3 |  | 1193 | 300 | 200 | 1440 |  | 200 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 12.54% | NA | 1971 | 187.3 | 65.54 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 187.3 |  | 0 | 0
1863500 | HPSS 1863500 | 499 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1966 | 22.4 | 62.16 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 22.4 | 0 |  | 0 | 0
1863530 | HPSS 1863530 | 499 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1993 | 24.3 | 60.66 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 24.3 |  | 0 | 0
4320771326 | HPSS 2522359 | 150 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 4.82% | 4.82% | 1964 | 409 | 60.32 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 409 | 0 |  | 0 | 0
1811600 | HPSS 1811600 | 499 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1994 | 15.1 | 60.16 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 15.1 |  | 0 | 0
14845 | Inlet 009-R-015 | 366 | 3 |  | 1193 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 9.20% | NA | 1968 | 7.3 | 59.7 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 7.3 | 0 |  | 0 | 0
1811611 | HPSS 1811611 | 499 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1996 | 60.2 | 59.16 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 60.2 |  | 0 | 0
1655 | Inlet M&R 25776 | 100 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 6.01% | 6.01% | 1989 | 28 | 59.01 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 28 |  | 0 | 0
9867583287 | Service Stub | 155 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1963 | 0 | 58.5 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 0 | 0 |  | 0 | 0
2522359 | HPSS 2522359 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1964 | 5 | 57.4 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 5 | 0 |  | 0 | 0
2522364 | HPSS 2522364 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1964 | 40.6 | 57.4 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 40.6 | 0 |  | 0 | 0
25775 | 2" Elma (RHD) H.P. Line | 100 | 3 |  | 499 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 2.20% | 6.01% | 1978 | 1572.7 | 57.01 | 116 Segment, Downrate | 2018 | 1 | 1 | 0 | 1572.7 |  | 0 | 0
C0067138 | Inlet 009-R-042 | 305 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 9.80% | 9.80% | 2001 | 29 | 56.8 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 29 |  | 0 | 0
19313 | Inlet 009-R-018 | 499 | 3 |  | 1549 | 100 | 66 | 1200 |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 9.66% | NA | 1971 | 9.1 | 56.66 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 9.1 |  | 0 | 0
1864030 | HPSS 1864030 | 499 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1971 | 3 | 56.66 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 3 |  | 0 | 0
10442 | Inlet 009-R-013 | 155 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.90% | NA | 1966 | 28.5 | 56.4 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 28.5 | 0 |  | 0 | 0
186015 | Inlet 009-R-055 | 499 | 3 |  | 1569 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 12.71% | 11.35% | 2011 | 32.2 | 55.71 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 32.2 |  | 0 | 0
1864029 | HPSS 1864029 | 499 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1980 | 5.2 | 52.16 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 5.2 |  | 0 | 0
C0068316 | 8" Kitsap Line | 366 | 3 |  | 811 | 950 | 633 | NA |  | 633 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 18.04% | 9.20% | 2002 | 176.2 | 50.54 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 176.2 |  | 0 | 0
C0074544 | 4" Satsop H.P. Line | 305 | 3 |  | 499 | 1000 | 666 | NA |  | 499 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 18.33% | 18.33% | 2005 | 151.8 | 49.33 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 151.8 |  | 0 | 0
2440103 | HPSS 2440103 | 305 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 1979 | 19 | 48.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
C0070660 | Inlet 009-R-043 | 250 | 3 |  | 1361 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2003 | 144.4 | 48.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 144.4 |  | 0 | 0
2083832 | Service Stub | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1964 | 42.1 | 48.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 42.1 | 0 |  | 0 | 0
2083850 | HPSS 2083850 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1964 | 69.1 | 48.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 69.1 | 0 |  | 0 | 0
2522365 | HPSS 2522365 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1964 | 37.1 | 48.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 37.1 | 0 |  | 0 | 0
1864070 | HPSS 1864070 | 499 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1989 | 15 | 47.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
186016 | Outlet 009-R-055 | 366 | 3 |  | 1553 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 9.33% | 9.43% | 2011 | 31.5 | 47.43 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 31.5 |  | 0 | 0
2084002 | Inlet 009-R-048 | 150 | 3 |  | 1549 | 100 | 66 | 275 |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.90% | NA | 1965 | 18 | 47.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 18 | 0 |  | 0 | 0
2083826 | Service Stub | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1965 | 42.1 | 47.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 42.1 | 0 |  | 0 | 0
2083836 | Service Stub | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1965 | 42.1 | 47.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 42.1 | 0 |  | 0 | 0
186014 | Outlet 009-R-055 | 366 | 3 |  | 1569 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NA | NA | 9.33% | NA | 2011 | 18.2 | 47.33 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18.2 |  | 0 | 0
2440105 | HPSS 2440105 | 135 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.61% | NA | 1965 | 30.7 | 47.11 | Addressed w/ 116 Segment | 2023 | 1 | 0 | 30.7 | 0 |  | 0 | 0
2250 | HPSS 2250 | 150 | 3 |  | 499 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 9.01% | NA | 1989 | 2 | 47.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
1820850 | HPSS 1820850 | 155 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1966 | 13.1 | 46.5 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 13.1 | 0 |  | 0 | 0
2522385 | HPSS 2522385 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1966 | 31.5 | 46.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 31.5 | 0 |  | 0 | 0
13617 | Inlet 009-R-003 | 150 | 3 |  | 1193 | 100 | 71 | 1200 |  | 71 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | YES | YES | 3.77% | 3.77% | 1967 | 39.6 | 46.27 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 39.6 | 0 |  | 0 | 0
1867002 | HPSS 1867002 | 499 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1992 | 30 | 46.16 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
1864071 | HPSS 1864071 | 499 | 3 |  | 1549 | 630 | 420 | UNKV |  | 420 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1993 | 14.7 | 45.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 14.7 |  | 0 | 0
2083818 | HPSS 2083818 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1967 | 42.1 | 45.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 42.1 | 0 |  | 0 | 0
2083820 | HPSS 2083820 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1967 | 42.1 | 45.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 42.1 | 0 |  | 0 | 0
2083830 | HPSS 2083830 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1967 | 18 | 45.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 18 | 0 |  | 0 | 0
2522180 | HPSS 2522180 | 150 | 3 |  | 1193 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.77% | NA | 1968 | 44.2 | 45.27 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 44.2 | 0 |  | 0 | 0
1863479 | HPSS 1863479 | 499 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1996 | 101.8 | 45.16 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 101.8 |  | 0 | 0
1850055 | HPSS 1850055 | 499 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1995 | 29.9 | 44.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 29.9 |  | 0 | 0
2083821 | HPSS 2083821 | 150 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1968 | 42 | 44.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 42 | 0 |  | 0 | 0
2522390 | HPSS 2522390 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1968 | 18.3 | 44.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 18.3 | 0 |  | 0 | 0
2363651033 | HPSS 2363651033 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1968 | 38.1 | 44.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 38.1 | 0 |  | 0 | 0
2083825 | HPSS 2083825 | 150 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1967 | 18 | 44.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 18 | 0 |  | 0 | 0
223505 - IN | Inlet 009-R-061 | 809 | 3 |  | 1792 | 2 | 1 | 1440 |  | 1 |  |  | UNVALID | 8.625 | 0.322 | 60000 | 0.8 | NO | NO | YES | 18.06% | 18.06% | 2015 | 70.5 | 44.06 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 70.5 |  | 0 | 0
1441720037 | HPSS 1441720037 | 250 | 3 |  | 933 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1993 | 54.5 | 44.03 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 54.5 |  | 0 | 0
47604 | Inlet 009-R-038 | 366 | 3 |  | 877 | 750 | 500 | NA |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 12.52% | 9.93% | 1994 | 44.6 | 44.02 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 44.6 |  | 0 | 0
1810852 | HPSS 1810852 | 155 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1969 | 12 | 43.5 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 12 | 0 |  | 0 | 0
19874 | Main Stub, 785-CA-011 | 155 | 3 |  | 933 | 100 | 66 | 250 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.41% | 4.98% | 1972 | 113.8 | 43.48 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 113.8 |  | 0 | 0
2083475 | HPSS 2083475 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1969 | 18 | 43.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 18 | 0 |  | 0 | 0
2522330 | HPSS 2522330 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1969 | 52 | 43.4 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 52 | 0 |  | 0 | 0
2522369 | Service Stub | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1969 | 43.6 | 43.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 43.6 | 0 |  | 0 | 0
2522410 | HPSS 2522410 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1969 | 43.2 | 43.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 43.2 | 0 |  | 0 | 0
1863511 | HPSS 1863511 | 499 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1998 | 57.1 | 43.16 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 57.1 |  | 0 | 0
39577 | Inlet 009-R-030 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 10.99% | 10.99% | 1993 | 14.7 | 42.99 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.7 |  | 0 | 0
47595 | Inlet 009-R-027 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 10.99% | 10.99% | 1994 | 22.4 | 42.49 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 22.4 |  | 0 | 0
2490045 | HPSS 2490045 | 305 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 1992 | 36 | 42.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
2083890 | HPSS 2083890 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1970 | 16.5 | 42.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 16.5 | 0 |  | 0 | 0
1863480 | HPSS 1863480 | 499 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1990 | 34.1 | 42.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.1 |  | 0 | 0
1863520 | HPSS 1863520 | 499 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1990 | 33.4 | 42.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 33.4 |  | 0 | 0
39870 | Inlet 009-R-021 | 125 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.02% | NA | 1991 | 39 | 41.02 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 39 |  | 0 | 0
2083855 | HPSS 2083855 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1971 | 18.1 | 40.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18.1 |  | 0 | 0
2521905 | HPSS 2521905 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1989 | 89 | 40.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 89 |  | 0 | 0
2490958 | HPSS 2490958 | 305 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 1996 | 40.8 | 40.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40.8 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1863487 | HPSS 1863487 | 499 | 3 |  | 1549 | 910 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2005 | 32.9 | 39.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 32.9 |  | 0 | 0
2083843 | HPSS 2083843 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1974 | 18 | 39.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
2083846 | HPSS 2083846 | 150 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1972 | 18 | 39.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
C0080941 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 973 | 830 | 553 | 720 |  | 553 | X |  | UNVALID | 8.625 | 0.25 | 42000 | 0.8 | NO | NO | YES | 12.53% | 11.67% | 2006 | 225.6 | 39.03 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 225.6 |  | 0 | 0
203116 | Inlet 009-R-050 | 150 | 3 |  | 2260 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 1.99% | NA | 1969 | 19 | 38.49 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 19 | 0 |  | 0 | 0
2440025 | HPSS 2440025 | 305 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 1991 | 39.8 | 37.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39.8 |  | 0 | 0
26452 | Main Stub | 100 | 3 |  | 933 | 100 | 66 | 250 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 2.20% | 3.21% | 1978 | 18 | 37.71 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 18 |  | 0 | 0
223505 - OUT | Outlet 009-R-061 | 305 | 3 |  | 1205 | 2 | 1 | 720 |  | 1 |  |  | UNVALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2015 | 181.8 | 37.12 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 181.8 |  | 0 | 0
2490046 | HPSS 2490046 | 305 | 3 |  | 1549 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 2003 | 17 | 36.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
2440036 | HPSS 2440040 | 135 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.61% | 2.61% | 1979 | 10 | 36.61 | Addressed w/ 116 Segment | 2023 | 1 | 1 | 0 | 10 |  | 0 | 0
45256 | Inlet 009-R-036 | 366 | 3 |  | 1361 | 750 | 500 | NA |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.06% | 8.06% | 1993 | 23.5 | 35.06 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 23.5 |  | 0 | 0
2440035 | HPSS 2440035 | 135 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.61% | NA | 1983 | 20 | 34.61 | Addressed w/ 116 Segment | 2023 | 1 | 1 | 0 | 20 |  | 0 | 0
46522 | Inlet 009-R-037 | 366 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.06% | NA | 1994 | 27.2 | 34.56 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 27.2 |  | 0 | 0
C0080671 | Inlet 009-R-054 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 21.7 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21.7 |  | 0 | 0
C0079627 | Inlet 009-R-046 | 305 | 3 |  | 933 | 905 | 603 | 1440 |  | 603 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 9.80% | 9.80% | 2006 | 9.2 | 34.3 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 9.2 |  | 0 | 0
2083831 | HPSS 2083831 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1985 | 18 | 33.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
1853460 | HPSS 1853460 | 125 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.42% | NA | 1985 | 58.1 | 33.42 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 58.1 |  | 0 | 0
1853450 | HPSS 1853450 | 125 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.42% | NA | 1984 | 47 | 32.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
2520004 | HPSS 2520004 | 305 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 2001 | 13 | 32.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
2520005 | HPSS 2520005 | 305 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 2001 | 15 | 32.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
2490020 | HPSS 2490020 | 100 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 1.94% | NA | 1986 | 51.2 | 32.44 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 51.2 |  | 0 | 0
2520001 | HPSS 2520001 | 305 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 2002 | 23 | 32.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23 |  | 0 | 0
2522347 | HPSS 2522347 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1988 | 39.9 | 32.4 | Addressed w/ 116 Segment | 2022 | 1 | 1 | 0 | 39.9 |  | 0 | 0
2083960 | HPSS 2083960 | 150 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1989 | 166 | 31.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 166 |  | 0 | 0
1854415 | HPSS 1854415 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 15 | 31.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
1854416 | HPSS 1854416 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 157 | 31.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 157 |  | 0 | 0
2520006 | HPSS 2520006 | 305 | 3 |  | 1549 | 755 | 503 | UNKV |  | 503 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 2004 | 20.3 | 31.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.3 |  | 0 | 0
2522360 | HPSS 2522360 | 150 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1990 | 118.6 | 31.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 118.6 |  | 0 | 0
2522366 | HPSS 2522366 | 150 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1991 | 201 | 30.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 201 |  | 0 | 0
1854425 | HPSS 1854425 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 20 | 30.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
29119 | Inlet 009-R-024 | 150 | 3 |  | 2260 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 1.99% | NA | 1982 | 10.4 | 30.49 | Addressed w/ 116 Segment | 2022 | 1 | 1 | 0 | 10.4 |  | 0 | 0
32090 | Inlet 009-R-051 | 155 | 3 |  | 1361 | 100 | 66 | 250 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.41% | NA | 1985 | 21.3 | 30.41 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21.3 |  | 0 | 0
2522416 | HPSS 2522416 | 305 | 3 |  | 1549 | 905 | 603 | UNKV |  | 603 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.90% | NA | 2006 | 23.4 | 30.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.4 |  | 0 | 0
2083827 | HPSS 2083827 | 150 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1990 | 18 | 30.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
2083828 | HPSS 2083828 | 150 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1990 | 59 | 30.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 59 |  | 0 | 0
1854417 | HPSS 1854417 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 19 | 30.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
1854600 | HPSS 1854600 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 80 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 80 |  | 0 | 0
1811700 | HPSS 1811700 | 155 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1991 | 19.1 | 30 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19.1 |  | 0 | 0
2490041 | HPSS 2490041 | 100 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 1.94% | NA | 1989 | 48.6 | 29.94 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48.6 |  | 0 | 0
2083854 | HPSS 2083854 | 150 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1991 | 30 | 29.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
1854601 | HPSS 1854601 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 73 | 29.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 73 |  | 0 | 0
172883 | Inlet 009-R-053 | 366 | 3 |  | 2123 | 100 | 66 | 720 |  | 66 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NO | YES | 5.17% | 5.17% | 2010 | 39.5 | 28.67 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 39.5 |  | 0 | 0
2083915 | HPSS 2083915 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1996 | 20 | 28.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
2083916 | HPSS 2083916 | 150 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1994 | 14 | 28.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
2522361 | HPSS 23189 | 150 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1994 | 8 | 28.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
2440037 | HPSS 2440037 | 135 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.61% | NA | 1994 | 22.1 | 28.11 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22.1 |  | 0 | 0
1853376 | HPSS 1853376 | 125 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.42% | NA | 1994 | 11.7 | 27.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11.7 |  | 0 | 0
2083823 | HPSS 2083823 | 150 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1995 | 60.1 | 27.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60.1 |  | 0 | 0
2083824 | HPSS 2083824 | 150 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1995 | 40.1 | 27.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.1 |  | 0 | 0
2522362 | HPSS 2522362 | 150 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1995 | 15 | 27.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
2490010 | HPSS 2490010 | 100 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 1.94% | NA | 1994 | 75 | 27.44 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 75 |  | 0 | 0
1853375 | HPSS 1853375 | 125 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.42% | NA | 1997 | 49 | 27.42 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
2083917 | HPSS 2083917 | 150 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1996 | 30 | 27.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
1841866 | HPSS 1841866 | 155 | 3 |  | 1549 | 200 | 133 | UNKV |  | 133 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1999 | 65 | 27 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 65 |  | 0 | 0
2490042 | HPSS 2490042 | 100 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 1.94% | NA | 1995 | 26.8 | 26.94 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26.8 |  | 0 | 0
1820825 | HPSS 1820825 | 155 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1999 | 10 | 26 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
2522325 | HPSS 2522325 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2001 | 8.2 | 25.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 8.2 |  | 0 | 0
2522322 | HPSS 2522322 | 150 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2000 | 10 | 25.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
2522367 | HPSS 2522367 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2003 | 20.6 | 24.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20.6 |  | 0 | 0
1854602 | HPSS 1854602 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 57.7 | 24.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.7 |  | 0 | 0
2522337 | HPSS 2522337 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2006 | 34 | 23.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 34 |  | 0 | 0
2083840 | HPSS 2083840 | 150 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2004 | 42.1 | 23.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.1 |  | 0 | 0
C0073773 | Inlet 009-R-044 | 125 | 3 |  | 933 | 250 | 166 | 1440 |  | 166 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 4.02% | 4.02% | 2007 | 50.5 | 23.02 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 50.5 |  | 0 | 0
2522171 | HPSS 2522171 | 150 | 3 |  | 1549 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2007 | 48.2 | 22.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 48.2 |  | 0 | 0
2083819 | HPSS 2083819 | 150 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2005 | 43 | 22.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
7730671104 | HPSS 7730671104 | 125 | 3 |  | 1193 | 87.5 | 58 | UNKV |  | 58 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.14% | NA | 2011 | 65 | 21.14 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 65 |  | 0 | 0
2082102 | HPSS 2082102 | 150 | 3 |  | 1549 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2009 | 25.1 | 20.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25.1 |  | 0 | 0
C0074005 | Inlet 009-R-045 | 150 | 3 |  | 1361 | 300 | 200 | 1440 |  | 200 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.30% | 3.30% | 2005 | 172.9 | 20.3 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 172.9 |  | 0 | 0
1923328816 | HPSS 1923328816 | 150 | 3 |  | 1193 | 760 | 506 | UNKV |  | 506 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.77% | NA | 2012 | 18 | 20.27 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
20C6308-T | 8" Kitsap Line | 499 | 3 |  | 802 | 750 | 535 | 720 |  | 535 | X | NA | VALID | 8.625 | 0.188 | 46000 | 0.8 | NO | YES | YES | 24.88% | 16.03% | 1964 | 66884.7 | 113.38 | Accept Most Stringent Criteria | -- | 1 | 0 | 66884.7 | 0 | 1 | 66884.7 | 0 | 1
75C6140 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 802 | 760 | 506 | NA |  | 506 | X | NA | VALID | 8.625 | 0.188 | 46000 | 0.8 | NO | NO | YES | 15.21% | 6.81% | 1964 | 143179.9 | 92.21 | Accept Most Stringent Criteria | -- | 1 | 0 | 143179.9 | 0 | 1 | 143179.9 | 0 | 1
907 | 4” Montesano H.P. Line | 305 | 3 |  | 499 | 790 | 526 | NA |  | 499 | X | NA | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 18.33% | NA | 1964 | 11441.5 | 89.33 | Accept Most Stringent Criteria | -- | 1 | 0 | 11441.5 | 0 | 1 | 11441.5 | 0 | 1
78C6314 | 4" Elma H.P. Line | 150 | 3 |  | 418 | 350 | 233 | 275 |  | 233 | X | NA | VALID | 8.625 | 0.322 | 46000 | 0.8 | NO | YES | YES | 9.01% | 14.34% | 1963 | 14907.3 | 86.34 | Accept Most Stringent Criteria | -- | 1 | 0 | 14907.3 | 0 | 1 | 14907.3 | 0 | 1
T0022504 | 8" Kitsap Line | 499 | 3 |  | 610 | 1080 | 720 | 1440 |  | 610 | X | X | VALID | 12.75 | 0.312 | 35000 | 0.8 | NO | NO | YES | 32.70% | 21.21% | 2000 | 790.3 | 86.2 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 790.3 | 1 | 0 | 790.3 |  | 1
75C6897 | 6" Aberdeen H.P. Line | 150 | 3 |  | 544 | 485 | 323 | NA |  | 323 | X | NA | VALID | 6.625 | 0.188 | 24000 | 0.8 | NO | NO | YES | 11.01% | 1.99% | 1965 | 6168.7 | 76.01 | Accept Most Stringent Criteria | -- | 1 | 0 | 6168.7 | 0 | 1 | 6168.7 | 0 | 1
20C6308 (V-001) | 8" Kitsap Line (009-V-001) | 499 | 3 |  | 1045 | 750 | 535 | 720 |  | 535 | X | NA | VALID | 8.625 | 0.322 | 46000 | 0.8 | NO | NO | YES | 14.53% | 19.09% | 1964 | 29.6 | 71.09 | Accept Most Stringent Criteria | -- | 1 | 0 | 29.6 | 0 | 1 | 29.6 | 0 | 1
59753 | 4" Satsop H.P. Line | 305 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X | X | VALID | 4.5 | 0.188 | 24000 | 0.6 | NO | YES | YES | 15.21% | 18.33% | 2001 | 33153.9 | 70.33 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 33153.9 | 1 | 0 | 33153.9 |  | 1
21C6309 | 4" Shelton H.P. Line | 155 | 3 |  | 499 | 350 | 250 | NA |  | 250 | X | NA | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 9.31% | 9.31% | 1969 | 12652.8 | 68.81 | Accept Most Stringent Criteria | -- | 1 | 0 | 12652.8 | 0 | 1 | 12652.8 | 0 | 1
19261 | 8" Kitsap Line | 366 | 3 |  | 732 | 780 | 520 | 720 |  | 520 | X | X | VALID | 8.625 | 0.188 | 42000 | 0.8 | NO | NO | YES | 19.99% | 14.01% | 1972 | 788.1 | 67.49 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 788.1 | 1 | 0 | 788.1 |  | 1
50200 | 12" Kitsap H.P. Line | 499 | 3 |  | 933 | 1080 | 720 | 1440 |  | 720 | X | X | VALID | 12.75 | 0.312 | 52000 | 0.8 | NO | YES | YES | 19.61% | 19.61% | 1996 | 9665.5 | 64.11 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 9665.5 | 1 | 0 | 9665.5 |  | 1
29512 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 811 | 510 | 340 | 720 |  | 340 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 15.03% | 11.67% | 1981 | 671.5 | 58.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 671.5 | 1 | 0 | 671.5 |  | 1
C0067358 | 12" Kitsap H.P. Line | 499 | 3 |  | 1411 | 1080 | 720 | NA |  | 720 | X | X | VALID | 12.75 | 0.375 | 60000 | 0.8 | NO | NO | YES | 14.14% | 14.14% | 2002 | 13992.9 | 56.64 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 13992.9 | 1 | 0 | 13992.9 |  | 1
23189 | 4" South Elma H.P. Line | 150 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.13% | 4.07% | 1975 | 6145.4 | 55.13 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6145.4 | 1 | 0 | 6145.4 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
14338 | 2" North Shelton H.P. Line | 125 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | NA | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 4.02% | 4.02% | 1968 | 1248.6 | 52.02 | Accept Most Stringent Criteria | -- | 1 | 0 | 1248.6 | 0 | 1 | 1248.6 | 0 | 1
14781 | 2" North Shelton H.P. Line | 125 | 3 |  | 933 | 180 | 128 | NA |  | 128 | X | NA | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 2.75% | 4.02% | 1968 | 1327.6 | 52.02 | Accept Most Stringent Criteria | -- | 1 | 0 | 1327.6 | 0 | 1 | 1327.6 | 0 | 1
40981 | 4" North Shelton H.P. Line | 250 | 3 |  | 877 | 600 | 400 | NA |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 8.55% | 1992 | 28678.8 | 51.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 28678.8 | 1 | 0 | 28678.8 |  | 1
183044 | 8" Kitsap Line | 499 | 3 |  | 973 | 850 | 566 | 720 |  | 566 | X | X | VALID | 8.625 | 0.25 | 42000 | 0.8 | NO | NO | YES | 20.49% | 12.85% | 2011 | 129.5 | 49.49 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 129.5 | 1 | 0 | 129.5 |  | 1
180758 | 12" Kitsap H.P. Line | 499 | 3 |  | 1223 | 1080 | 720 | 720 |  | 720 | X | X | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NO | YES | 16.31% | 16.31% | 2011 | 5930.6 | 49.31 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5930.6 | 1 | 0 | 5930.6 |  | 1
58317, 57697 | 009-V-060, 061, 062, 063 | 499 | 3 |  | 1017 | 1080 | 720 | 720 |  | 720 | X | X | VALID | 12.75 | 0.312 | 52000 | 0.8 | NO | NO | YES | 19.61% | 19.61% | 2000 | 161 | 49.11 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 161 | 1 | 0 | 161 |  | 1
13523 | 2" North Shelton H.P. Line | 125 | 3 |  | 1361 | 600 | 400 | NA |  | 400 | X | NA | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 2.75% | NA | 1968 | 2997.2 | 46.75 | Accept Most Stringent Criteria | -- | 1 | 0 | 2997.2 | 0 | 1 | 2997.2 | 0 | 1
SS000329 | 8" Kitsap Line (009-V-068, 069, 070) | 499 | 3 |  | 1045 | 1080 | 720 | 720 |  | 720 | X | X | VALID | 8.625 | 0.322 | 46000 | 0.8 | NO | NO | YES | 14.53% | 19.09% | 2002 | 40.9 | 46.59 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 40.9 | 1 | 0 | 40.9 |  | 1
182291 | 8" Kitsap Line | 499 | 3 |  | 1045 | 852 | 568 | 720 |  | 568 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | YES | YES | 16.55% | 19.09% | 2012 | 108.4 | 46.59 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 108.4 | 1 | 0 | 108.4 |  | 1
46558 | 8" Kitsap Line | 366 | 3 |  | 1045 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.277 | 46000 | 0.8 | NO | NO | YES | 12.39% | 14.01% | 1994 | 472.2 | 46.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 472.2 | 1 | 0 | 472.2 |  | 1
24986 | 4" Shelton H.P. Line | 155 | 3 |  | 877 | 500 | 333 | 720 |  | 333 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.30% | 4.20% | 1977 | 112.8 | 45.3 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 112.8 | 1 | 0 | 112.8 |  | 1
40981-366 | Inlet 009-R-034 | 366 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 12.52% | 9.93% | 1992 | 25.3 | 45.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25.3 | 1 | 0 | 25.3 |  | 1
36730 | 6" Aberdeen H.P. Line | 150 | 3 |  | 794 | 525 | 350 | 720 |  | 350 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 7.55% | 5.07% | 1989 | 1432.3 | 44.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1432.3 | 1 | 0 | 1432.3 |  | 1
41470 | Inlet 009-R-033 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 10.99% | NA | 1992 | 35 | 43.49 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35 | 1 | 0 | 35 |  | 1
41120 | Inlet 009-R-019 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 10.99% | NA | 1994 | 31.6 | 42.49 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 31.6 | 1 | 0 | 31.6 |  | 1
SS000329 | 8" Kitsap Line (009-V-068, 069, 070) | 366 | 3 |  | 1373 | 1080 | 720 | NA |  | 720 | X | X | VALID | 8.625 | 0.322 | 46000 | 0.8 | NO | NA | NA | 14.53% | NA | 2002 | 17.7 | 42.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 17.7 | 1 | 0 | 17.7 |  | 1
SS000328 | 12" Kitsap Line (009-V-068, 069, 070) | 499 | 3 |  | 1411 | 1080 | 720 | 1440 |  | 720 | X | X | VALID | 12.75 | 0.375 | 60000 | 0.8 | NO | NO | YES | 14.14% | 14.14% | 2002 | 16 | 41.64 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 16 | 1 | 0 | 16 |  | 1
23792 | 2" North Shelton H.P. Line | 125 | 3 |  | 1361 | 600 | 400 | 250 |  | 250 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 2.75% | 2.75% | 1975 | 1788.3 | 41.25 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1788.3 | 1 | 0 | 1788.3 |  | 1
181677 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 637 | 424 | 720 |  | 424 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2011 | 1132.7 | 40.62 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1132.7 | 1 | 0 | 1132.7 |  | 1
34477 | 4" Elma (R.H.D.) H.P. Loop Line | 100 | 3 |  | 877 | 150 | 100 | 1440 |  | 100 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 3.42% | 2.71% | 1989 | 1444.1 | 38.92 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1444.1 | 1 | 0 | 1444.1 |  | 1
176437 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 840 | 560 | 720 |  | 560 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2011 | 847.2 | 38.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 847.2 | 1 | 0 | 847.2 |  | 1
181678 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 640 | 426 | 720 |  | 426 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2011 | 656.4 | 38.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 656.4 | 1 | 0 | 656.4 |  | 1
181679 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 645 | 430 | 720 |  | 430 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2011 | 582.7 | 38.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 582.7 | 1 | 0 | 582.7 |  | 1
183985 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 640 | 426 | 720 |  | 426 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2011 | 581.3 | 38.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 581.3 | 1 | 0 | 581.3 |  | 1
185510 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 641 | 427 | 720 |  | 427 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2011 | 591 | 38.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 591 | 1 | 0 | 591 |  | 1
30702 | 4" Elma H.P. Line | 150 | 3 |  | 877 | 600 | 400 | 400 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.13% | 4.07% | 1983 | 29.3 | 37.13 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 29.3 | 1 | 0 | 29.3 |  | 1
188090 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 630 | 420 | 720 |  | 420 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2013 | 925.4 | 37.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 925.4 | 1 | 0 | 925.4 |  | 1
210746 | 009-V101, 102, 103 | 809 | 3 |  | 2426 | 1275 | 850 | 1440 |  | 850 | X | X | VALID | 8.625 | 0.322 | 65000 | 1 | NO | NO | NO | 16.67% | 16.67% | 2014 | 51.7 | 36.17 | No Action Needed | -- | 1 | 1 | 0 | 51.7 | 1 | 0 | 51.7 |  | 1
186540 | Outlet 009-R-057 | 499 | 3 |  | 1553 | 1100 | 733 | 720 |  | 720 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 12.71% | 12.85% | 2012 | 22.7 | 35.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 22.7 | 1 | 0 | 22.7 |  | 1
186535 | Inlet 009-R-056 | 499 | 3 |  | 1569 | 1092 | 728 | 720 |  | 720 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 12.71% | 11.35% | 2012 | 50.4 | 35.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 50.4 | 1 | 0 | 50.4 |  | 1
186538 | Outlet 009-R-057 | 499 | 3 |  | 1569 | 1100 | 733 | NA |  | 733 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 12.71% | 11.35% | 2012 | 50.9 | 35.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 50.9 | 1 | 0 | 50.9 |  | 1
186539 | Inlet 009-R-057 | 499 | 3 |  | 1569 | 1100 | 733 | 720 |  | 720 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 12.71% | 11.35% | 2012 | 39.2 | 35.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 39.2 | 1 | 0 | 39.2 |  | 1
178875 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 859 | 572 | 720 |  | 572 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2010 | 439.9 | 34.62 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 439.9 | 1 | 0 | 439.9 |  | 1
181676 | 8" Grays Harbor H.P. Line | 305 | 3 |  | 1205 | 640 | 426 | 720 |  | 426 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.12% | 7.86% | 2011 | 455.3 | 34.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 455.3 | 1 | 0 | 455.3 |  | 1
52659 | Inlet 009-R-040 | 366 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.06% | NA | 1997 | 46.4 | 33.06 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 46.4 | 1 | 0 | 46.4 |  | 1
186757 | 009-R-058 | 305 | 3 |  | 1045 | 769 | 512 | 720 |  | 512 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 11.67% | 7.86% | 2016 | 86.7 | 32.17 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 86.7 | 1 | 0 | 86.7 |  | 1
1853445 | Inlet 009-R-029 | 125 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | Service | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.02% | NA | 1990 | 54.9 | 31.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 54.9 | 1 | 0 | 54.9 |  | 1
51987 | Inlet 009-R-039 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1997 | 132.1 | 31.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 132.1 | 1 | 0 | 132.1 |  | 1
35967 | Inlet 009-R-028 | 125 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 2.75% | NA | 1988 | 29.8 | 27.25 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 29.8 | 1 | 0 | 29.8 |  | 1
186534 | Outlet 009-R-056 | 366 | 3 |  | 1553 | 1092 | 728 | NA |  | 728 | X | X | VALID | 8.625 | 0.322 | 52000 | 0.8 | NO | NO | YES | 9.43% | 9.43% | 2012 | 24.7 | 26.93 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 24.7 | 1 | 0 | 24.7 |  | 1
186536 | Outlet 009-R-056 | 366 | 3 |  | 1553 | 1092 | 728 | 720 |  | 720 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 9.33% | 9.43% | 2012 | 55.4 | 26.93 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 55.4 | 1 | 0 | 55.4 |  | 1
40412 | Inlet 009-R-031 | 150 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.30% | 3.30% | 1991 | 58 | 26.3 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 58 | 1 | 0 | 58 |  | 1
189325 | Inlet 009-R-059 | 305 | 3 |  | 1361 | 800 | 533 | 720 |  | 533 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 6.72% | 6.72% | 2012 | 29.1 | 24.22 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 29.1 | 1 | 0 | 29.1 |  | 1
189011 - IN | Inlet 009-R-059 | 305 | 3 |  | 1361 | 750 | 500 | NA |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.72% | NA | 2012 | 1.5 | 24.22 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1.5 | 1 | 0 | 1.5 |  | 1
38437 | 009-V-018 (Inlet 009-R-029) | 125 | 3 |  | NA | NA | NA | 1440 |  | 1440 | X | Service | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1990 | 0 | 23.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
41636 | 009-V-024 (Inlet 009-R-035) | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X | Service | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1993 | 0 | 22 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
189380 | Inlet 009-R-060 | 150 | 3 |  | 1052 | 400 | 266 | 720 |  | 266 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 4.27% | 4.07% | 2013 | 22.9 | 16.27 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 22.9 | 1 | 0 | 22.9 |  | 1
189326 | Outlet 009-R-059 | 100 | 3 |  | 1052 | 280 | 186 | 275 |  | 186 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 2.85% | 2.71% | 2012 | 48 | 15.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 48 | 1 | 0 | 48 |  | 1
189011 - OUT | Outlet 009-R-059 | 100 | 3 |  | 1327 | 225 | 150 | NA |  | 150 | X | X | VALID | 4.5 | 0.237 | 42000 | 0.6 | NO | NA | NA | 2.26% | NA | 2012 | 3.5 | 14.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3.5 | 1 | 0 | 3.5 |  | 1
230683 | 4" Shelton H.P. Line | 155 | 3 |  | 1106 | 615 | 410 | 720 |  | 410 | X | X | VALID | 4.5 | 0.237 | 52000 | 0.6 | NO | NO | YES | 2.83% | 4.20% | 2016 | 46.1 | 14.7 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 46.1 | 1 | 0 | 46.1 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1281900 | HPSS 454800372 | 380 | 3 |  | NA | NA | NA | 720 |  | 720 | X | Service | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2015 | 0 | 11 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
28563-600 | Inlet 005-R-133 | 600 | 3 |  | NA | NA | NA | 1440 |  | 1440 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1980 | 0 | 28.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
484900321 | HPSS 484900321 | 250 | 3 |  | NA | NA | NA | UNKV |  | UNKV | X | Service | UNVALID | 1.05 | NA | NA | NA | YES | NA | NA | NA | NA | 1990 | 0 | 23.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 0 |  | 0 | 0
WR45525 | HPSS 1144089 | 150 | 3 |  | 1494 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | NA | NA | NA | NO | YES | YES | NA | 3.01% | 2003 | 104.5 | 35.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 104.5 |  | 0 | 0
18736 | 005-V-145, 005-O-002 | 600 | 3 |  | 446 | 900 | 600 | 720 |  | 446 |  |  | UNVALID | 16 | 0.25 | 52000 | 0.8 | NO | YES | YES | 53.75% | 53.33% | 1971 | 38.8 | 130.75 | In-Situ Test | 2018-2019 | 1 | 1 | 0 | 38.8 |  | 0 | 0
17930 | Inlet 005-R-008 | 150 | 4 |  | 635 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | NA | NA | 7.55% | NA | 1970 | 2 | 69.05 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 2 | 0 |  | 0 | 0
860124 | HPSS 860124 | 150 | 4 |  | 1239 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1965 | 29 | 58.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 29 | 0 |  | 0 | 0
42512 | 20" Sumas Transmission Line | 780 | 3 |  | 780 | 1170 | 780 | 1440 |  | 780 | X | X | VALID | 20 | 0.375 | 52000 | 0.8 | NO | NO | YES | 40.00% | 40.00% | 1993 | 17523.3 | 117 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 17523.3 | 1 | 0 | 17523.3 |  | 1
18794 | 16" N. Whatcom Transmission Line | 600 | 3 |  | 812 | 930 | 620 | 720 |  | 620 | X | X | VALID | 16 | 0.25 | 52000 | 1 | NO | YES | YES | 36.92% | 25.81% | 1971 | 143669 | 143.92 | No Action Needed | -- | 1 | 1 | 0 | 143669 | 1 | 0 | 143669 |  | 1
26956 | 12" Grandview Rd Transmission Line | 600 | 3 |  | 658 | 900 | 600 | 720 |  | 600 | X | X | VALID | 12.75 | 0.25 | 42000 | 0.8 | NO | NO | YES | 36.43% | 29.14% | 1980 | 7644.9 | 104.93 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7644.9 | 1 | 0 | 7644.9 |  | 1
1284820 | Inlet M&R 26955 | 600 | 3 |  | 658 | 900 | 600 | NA |  | 600 | X | Service | VALID | 12.75 | 0.25 | 42000 | 0.8 | NO | NO | YES | 36.43% | 29.14% | 1980 | 21 | 94.93 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21 | 1 | 0 | 21 |  | 1
40855 | 8" Central Whatcom H.P. Line | 380 | 3 |  | 418 | 680 | 453 | UNKV |  | 418 | X | X | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | NA | NA | 36.32% | NA | 1993 | 10573.7 | 122.32 | 116 Segment, In-Situ | 2017 | 1 | 1 | 0 | 10573.7 |  | 0 | 0
14C1344 | 8" Central Whatcom H.P. Line | 380 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 36.32% | 36.32% | 1957 | 53839.4 | 191.82 | 116 Segment, Pressure Test | 2018 | 1 | 0 | 53839.4 | 0 |  | 0 | 0
18734-1 | 8” Lake Terrell Rd Transmission Line | 380 | 3 |  | 418 | 569 | 379 | 720 |  | 379 |  | NA | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 36.32% | 36.32% | 1965 | 10414.9 | 138.82 | 116 Segment, In-Situ | 2017 | 1 | 0 | 10414.9 | 0 |  | 0 | 0
Line 1-1 | 8" Bellingham Transmission Line | 380 | 3 |  | 418 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 36.32% | NA | 1956 | 15434.1 | 187.82 | 116 Segment, Replace | 2018 | 1 | 0 | 15434.1 | 0 |  | 0 | 0
Line 1-1 | 8" Bellingham Transmission Line (005-V-149) | 380 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 36.32% | NA | 1956 | 13.2 | 172.82 | 116 Segment, Replace | 2018 | 1 | 0 | 13.2 | 0 |  | 0 | 0
42491 | 20" Ferndale Transmission Line | 600 | 3 |  | 780 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 20 | 0.375 | 52000 | 0.8 | NO | NO | YES | 30.77% | 30.77% | 1993 | 28254.9 | 97.77 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 28254.9 | 1 | 0 | 28254.9 |  | 1
41508 | 16" Squalicum Transmission Line | 250 | 4 |  | 269 | 600 | 400 | NA |  | 269 | X | X | VALID | 16 | 0.281 | 24000 | 0.8 | NO | NA | NA | 29.66% | NA | 1993 | 2596.5 | 100.16 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2596.5 | 1 | 0 | 2596.5 |  | 1
31567 | 005-V-043 | 600 | 3 |  | 811 | 900 | 600 | 720 |  | 600 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 29.57% | 22.96% | 1984 | 0 | 81.07 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
18734-2 | 8” Kickerville Transmission Line | 600 | 3 |  | 906 | 900 | 600 | 720 |  | 600 | X | X | VALID | 8.625 | 0.188 | 52000 | 0.8 | NO | NA | NA | 26.47% | NA | 1971 | 17358.8 | 99.47 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 17358.8 | 1 | 0 | 17358.8 |  | 1
34405 - 600 | Inlet 005-R-087 | 600 | 3 |  | 877 | 900 | 600 | 720 |  | 600 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 20.52% | 16.27% | 1987 | 1300.3 | 68.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1300.3 | 1 | 0 | 1300.3 |  | 1
25797 | Inlet 005-R-065 | 600 | 3 |  | 877 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 20.52% | 16.27% | 1978 | 5.3 | 65.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5.3 | 1 | 0 | 5.3 |  | 1
29520 | Inlet 005-R-073 | 600 | 3 |  | 877 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 20.52% | 16.27% | 1982 | 226.3 | 64.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 226.3 | 1 | 0 | 226.3 |  | 1
33880 | 4" West Lynden Transmission Line | 600 | 3 |  | 877 | 900 | 600 | 720 |  | 600 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 20.52% | 16.27% | 1988 | 1340.4 | 67.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1340.4 | 1 | 0 | 1340.4 |  | 1
163891 | Inlet 005-R-163 | 600 | 3 |  | 933 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 19.28% | 19.28% | 2009 | 25.1 | 67.28 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 25.1 |  | 0 | 0
52482 | Inlet 005-R-155 | 600 | 3 |  | 933 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NO | YES | 19.28% | 13.22% | 1997 | 21 | 53.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21 | 1 | 0 | 21 |  | 1
45634 | 8" Lake Terrell Rd Transmission Line | 380 | 3 |  | 802 | 740 | 493 | 720 |  | 493 | X | X | VALID | 8.625 | 0.188 | 46000 | 0.8 | NO | NO | YES | 18.95% | 14.54% | 1993 | 394.6 | 51.95 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 394.6 | 1 | 0 | 394.6 |  | 1
41506 | 005-V-093 | 380 | 3 |  | 784 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 18.73% | 15.99% | 1992 | 33.2 | 51.23 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 33.2 | 1 | 0 | 33.2 |  | 1
41501 | 10" Squalicum H.P. Line | 380 | 3 |  | 855 | 600 | 400 | UNKV |  | 400 | X | X | UNVALID | 10.75 | 0.25 | 46000 | 0.8 | YES | NO | YES | 17.76% | 15.99% | 1992 | 14960.3 | 65.26 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14960.3 |  | 0 | 0
42176 | Inlet 005-R-109 | 780 | 3 |  | 1361 | 1170 | 780 | 1440 |  | 780 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 17.18% | 17.18% | 1995 | 117 | 49.18 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 117 | 1 | 0 | 117 |  | 1
42177 | Inlet 005-R-110 | 780 | 3 |  | 1361 | 1200 | 800 | 1440 |  | 800 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 17.18% | 17.18% | 1995 | 54.2 | 48.18 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 54.2 |  | 0 | 0
18734-3 | 8” South Kickerville Transmission Line | 380 | 3 |  | 906 | 900 | 600 | 720 |  | 600 | X | X | VALID | 8.625 | 0.188 | 52000 | 0.8 | NO | NA | NA | 16.76% | NA | 1971 | 7141.9 | 69.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7141.9 | 1 | 0 | 7141.9 |  | 1
41502 | M&R 41502 | 250 | 4 |  | 451 | 600 | 400 | 275 |  | 275 | X | X | VALID | 12.75 | 0.25 | 46000 | 0.8 | NO | YES | YES | 16.38% | 17.71% | 1992 | 315.6 | 57.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 315.6 | 1 | 0 | 315.6 |  | 1
174995 | 10" Squalicum H.P. Line | 380 | 3 |  | 950 | 750 | 500 | 720 |  | 500 | X | X | VALID | 10.75 | 0.25 | 52000 | 1 | NO | NO | YES | 15.71% | 15.99% | 2010 | 1510.7 | 46.99 | No Action Needed | -- | 1 | 1 | 0 | 1510.7 | 1 | 0 | 1510.7 |  | 1
210697 | 10" Squalicum H.P. Line | 380 | 3 |  | 967 | 800 | 533 | 720 |  | 533 | X | X | VALID | 10.75 | 0.25 | 52000 | 0.8 | NO | YES | YES | 15.71% | 10.76% | 2014 | 923.2 | 46.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 923.2 | 1 | 0 | 923.2 |  | 1
27163 | 005-V-039 | 380 | 3 |  | 728 | 600 | 400 | 500 |  | 400 | X | X | VALID | 4.5 | 0.156 | 35000 | 0.6 | NO | NO | YES | 15.66% | 10.31% | 1979 | 35.1 | 58.66 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35.1 | 1 | 0 | 35.1 |  | 1
Line 4-1 | 4" South Lynden H.P. Line | 250 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 15.02% | NA | 1961 | 35395.5 | 114.02 | 116 Segment, Pressure Test | 2020 | 1 | 0 | 35395.5 | 0 |  | 0 | 0
1391000 | Inlet 005-R-069 | 250 | 3 |  | 499 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 15.02% | NA | 1982 | 47 | 61.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 47 |  | 0 | 0
4059 | Inlet 005-R-028 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 1961 | 12.4 | 94.02 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 12.4 | 0 |  | 0 | 0
218481 | 4" Blaine H.P. Line | 250 | 3 |  | 499 | 684 | 456 | 720 |  | 456 | X | X | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NO | YES | 15.02% | 4.56% | 2015 | 1604.5 | 47.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1604.5 | 1 | 0 | 1604.5 |  | 1
AA00894 | 005-V-168 | 250 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 8.03% | 2002 | 21.1 | 46.52 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 21.1 |  | 0 | 0
UNKV (005-O-010) | 005-O-010 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 1961 | 91.6 | 94.02 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 91.6 | 0 |  | 0 | 0
59131 | 8" Bellingham Transmission Line | 380 | 3 |  | 1045 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.322 | 35000 | 0.8 | NO | NO | YES | 14.54% | 14.54% | 2000 | 225.1 | 44.04 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 225.1 | 1 | 0 | 225.1 |  | 1
FISH | Bellingham HP Distribution System | 150 | 4 |  | 268 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 10.75 | 0.25 | 24000 | 0.8 | YES | YES | YES | 14.34% | 17.87% | 1954 | 28793.6 | 120.87 | 116 Segment, Replace | 2019 | 1 | 0 | 28793.6 | 0 |  | 0 | 0
11406 | Outlet 005-R-018 | 150 | 3 |  | 335 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 10.75 | 0.25 | 24000 | 0.8 | YES | YES | YES | 14.34% | 17.87% | 1966 | 80.7 | 91.87 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 80.7 | 0 |  | 0 | 0
11406-T | Inlet 005-R-018 | 150 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 14.34% | 9.01% | 1956 | 72.4 | 98.34 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 72.4 | 0 |  | 0 | 0
55653 | Inlet 005-R-134 | 780 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 |  |  | UNVALID | 2.375 | 0.154 | 42000 | 0.6 | NO | NO | YES | 14.32% | 17.18% | 1999 | 17 | 51.18 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 17 |  | 0 | 0
25773 | 4" North Lynden H.P. Line | 400 | 3 |  | 877 | 600 | 400 | 250 |  | 250 |  | X | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 13.68% | 10.85% | 1978 | 7689.3 | 63.18 | 116 Segment, Expose/Verify | 2016 | 1 | 1 | 0 | 7689.3 |  | 0 | 0
21602 | Main Stub | 600 | 3 |  | 1361 | 900 | 600 | 250 |  | 250 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 13.22% | NA | 1973 | 1.5 | 65.22 | Expose/Verify/Replace | 2018-2023 | 1 | 1 | 0 | 1.5 |  | 0 | 0
21252 | Inlet 005-R-040 | 600 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 13.22% | NA | 1973 | 3.7 | 60.22 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 3.7 |  | 0 | 0
22140 | Inlet 005-R-047 | 600 | 3 |  | 1193 | 600 | 400 | 1440 |  | 400 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 13.22% | 15.08% | 1973 | 15.5 | 66.08 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 15.5 |  | 0 | 0
22158 | Inlet 005-R-044 | 600 | 3 |  | 1193 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 13.22% | 15.08% | 1973 | 9.7 | 66.08 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 9.7 |  | 0 | 0
22213 | Inlet 005-R-046 | 600 | 3 |  | 1193 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 13.22% | 15.08% | 1973 | 7.7 | 66.08 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 7.7 |  | 0 | 0
22857 | Inlet 005-R-021 | 600 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 13.22% | NA | 1974 | 14.7 | 59.72 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 14.7 |  | 0 | 0
33963 | Inlet 005-R-043 | 600 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 13.22% | NA | 1973 | 13.4 | 60.22 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 13.4 |  | 0 | 0
34572 | Inlet 005-R-089 | 600 | 3 |  | 1361 | 100 | 66 | 720 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1987 | 57.8 | 53.22 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 57.8 |  | 0 | 0
54538 | Inlet 005-R-133 | 600 | 3 |  | 1361 | 750 | 500 | 720 |  | 500 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1998 | 230.4 | 48.72 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 230.4 |  | 0 | 0
19466 - 600 | Inlet 005-R-041 | 600 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1973 | 146.1 | 61.22 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 146.1 |  | 0 | 0
36794 | Inlet 005-R-094 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 13.22% | NA | 1989 | 36.1 | 47.22 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 36.1 | 1 | 0 | 36.1 |  | 1
38943 | Inlet 005-R-099 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1991 | 124.6 | 47.22 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 124.6 | 1 | 0 | 124.6 |  | 1
41012 | Inlet 005-R-103 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1992 | 25 | 45.72 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
41621 | Inlet 005-R-106 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1992 | 32.6 | 45.72 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 32.6 | 1 | 0 | 32.6 |  | 1
43624 | Inlet 005-R-107 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 13.22% | NA | 1993 | 19.8 | 45.22 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 19.8 | 1 | 0 | 19.8 |  | 1
51215 | Inlet 005-R-130 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1997 | 602.9 | 48.22 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 602.9 | 1 | 0 | 602.9 |  | 1
55461 | Inlet 005-R-137 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 2000 | 40.7 | 41.72 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 40.7 | 1 | 0 | 40.7 |  | 1
224325 | 005-V-258 | 600 | 3 |  | 1361 | 900 | 600 | 720 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 2015 | 0 | 34.22 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
34400 | Inlet 005-R-079 | 600 | 3 |  | 1106 | 900 | 600 | 1440 |  | 600 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 16.27% | 1986 | 71.2 | 51.77 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 71.2 |  | 0 | 0
36385 | Inlet 005-R-093 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 1988 | 8.9 | 47.72 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 8.9 |  | 0 | 0
47667 | Inlet 005-R-125 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 13.22% | NA | 1995 | 42.6 | 44.22 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 42.6 |  | 0 | 0
A0067513 | Inlet 005-R-149 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 2002 | 25.1 | 40.72 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 25.1 |  | 0 | 0
A0071244 | Inlet 005-R-151 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 2003 | 28.2 | 40.22 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 28.2 |  | 0 | 0
A0071903 | Inlet 005-R-152 | 600 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 2005 | 7 | 39.22 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 7 |  | 0 | 0
A0078097 | Inlet 005-R-155 | 600 | 3 |  | 1361 | 900 | 600 | NA |  | 600 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 13.22% | 13.22% | 2005 | 6.5 | 39.22 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 6.5 |  | 0 | 0
14C5522 | 4" Ferndale H.P. Line | 380 | 3 |  | 877 | 600 | 400 | UNKV |  | 400 | X | NA | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | NA | NA | 12.99% | NA | 1962 | 8104.3 | 76.99 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 8104.3 | 0 |  | 0 | 0
45948 | Inlet 005-R-121 | 380 | 3 |  | 877 | 680 | 453 | UNKV |  | 453 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | NO | YES | 12.99% | 10.31% | 1995 | 39.6 | 43.99 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39.6 |  | 0 | 0
217876 | 8" Bellingham Transmission Line | 380 | 3 |  | 1205 | 660 | 440 | NA |  | 440 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NA | NA | 12.61% | NA | 2015 | 8 | 33.61 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 8 | 1 | 0 | 8 |  | 1
41505 | 12", 16" & 4" Squalicum H.P. Line | 250 | 4 |  | 525 | 600 | 400 | 275 |  | 275 | X | X | VALID | 12.75 | 0.25 | 52000 | 0.8 | NO | YES | YES | 12.26% | 15.24% | 1993 | 20999.1 | 68.24 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20999.1 | 1 | 0 | 20999.1 |  | 1
1281920 | Inlet 005-R-061 | 380 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 12.21% | NA | 1982 | 24.9 | 73.71 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 24.9 |  | 0 | 0
13541 | Inlet 005-R-022 | 380 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 12.21% | 12.21% | 1968 | 45.8 | 84.21 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 45.8 | 0 |  | 0 | 0
44543 | Inlet 005-R-119 | 380 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 12.21% | NA | 1993 | 26 | 48.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 26 | 1 | 0 | 26 |  | 1
56120 | Inlet 005-R-138 | 380 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 12.21% | NA | 1998 | 30.9 | 45.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 30.9 | 1 | 0 | 30.9 |  | 1
180093 | Inlet 005-R-166 | 380 | 3 |  | 933 | 800 | 533 | 1440 |  | 533 | X | Service | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 12.21% | 12.21% | 2010 | 13 | 39.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 13 | 1 | 0 | 13 |  | 1
3716127268 | HPSS 3716127268 | 380 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 12.21% | NA | 2011 | 39 | 39.21 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
7766800126 | Service Stub | 380 | 3 |  | 933 | 625 | 416 | UNKV |  | 416 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 12.21% | 12.21% | 2016 | 6.7 | 36.71 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6.7 |  | 0 | 0
23799 | 8" Central Whatcom H.P. Line | 380 | 3 |  | 933 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 12.21% | 12.21% | 1975 | 197.3 | 58.21 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 197.3 |  | 0 | 0
A0071883 | Main Stub (R-152) | 600 | 3 |  | 1549 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 11.62% | 11.62% | 2005 | 0 | 46.62 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 0 |  | 0 | 0
1240105 | HPSS 1240105 | 600 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1973 | 53 | 62.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 53 |  | 0 | 0
1240540 | HPSS 3386800317 | 600 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1973 | 53.8 | 62.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 53.8 |  | 0 | 0
1240610 | HPSS 1240610 | 600 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1975 | 97.8 | 61.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 97.8 |  | 0 | 0
1280157 | HPSS 1280157 | 600 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1994 | 13 | 52.12 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 13 |  | 0 | 0
1280181 | HPSS 1280181 | 600 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1994 | 46 | 52.12 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 46 |  | 0 | 0
1289702 | HPSS 1289702 | 600 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 79.4 | 53.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 79.4 |  | 0 | 0
1326507 | HPSS 1326507 | 600 | 3 |  | 1549 | 90 | 64 | UNKV |  | 64 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1970 | 9 | 66.62 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 9 | 0 |  | 0 | 0
3988700204 | HPSS 3988700204 | 600 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1971 | 14.9 | 63.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 14.9 |  | 0 | 0
1281448 | HPSS 1281448 | 600 | 3 |  | 1549 | 930 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 2004 | 10 | 47.12 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
1284779 | HPSS 1284779 | 600 | 3 |  | 1549 | 950 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 11.62% | NA | 2006 | 19 | 46.12 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
1247597 | Inlet M&R 9021 | 600 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1971 | 17.9 | 78.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 17.9 |  | 0 | 0
1280539 | HPSS 1280539 | 600 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1998 | 63 | 65.12 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 63 |  | 0 | 0
1326911 | HPSS 8181900761 | 600 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1997 | 22 | 75.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 22 |  | 0 | 0
2646620005 | HPSS 2646620005 | 600 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1983 | 68.2 | 72.62 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 68.2 |  | 0 | 0
1240080 | HPSS 1240080 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1972 | 7 | 58.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
1240100 | HPSS 1240100 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1987 | 31.5 | 50.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31.5 |  | 0 | 0
1240145 | HPSS 1240145 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1988 | 160.1 | 51.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 160.1 |  | 0 | 0
1240155 | HPSS 1240155 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1986 | 90 | 51.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 90 |  | 0 | 0
1240495 | HPSS 1240495 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1998 | 17 | 45.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
1240521 | HPSS 1240521 | 600 | 3 |  | 1549 | 1000 | 666 | UNKV |  | 666 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1990 | 133.3 | 50.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 133.3 |  | 0 | 0
1240524 | HPSS 1240524 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1996 | 67.1 | 46.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 67.1 |  | 0 | 0
1240529 | HPSS 1240529 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1989 | 75 | 49.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 75 |  | 0 | 0
1240530 | HPSS 1240530 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1978 | 76.1 | 55.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 76.1 |  | 0 | 0
1240535 | HPSS 1307825 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 11.62% | 11.62% | 1996 | 101.6 | 47.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 101.6 |  | 0 | 0
1240542 | HPSS 1240542 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 26.8 | 48.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26.8 |  | 0 | 0
1240545 | HPSS 1240545 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1982 | 39 | 53.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39 |  | 0 | 0
1240820 | HPSS 6398700319 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1971 | 15 | 58.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
1247554 | HPSS 1247554 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1993 | 80.9 | 47.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 80.9 |  | 0 | 0
1247555 | HPSS 1247555 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 11.62% | 11.62% | 1993 | 78.6 | 47.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 78.6 |  | 0 | 0
1247557 | HPSS 1247557 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1993 | 74.1 | 47.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 74.1 |  | 0 | 0
1247601 | HPSS 1247601 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1994 | 20 | 47.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1280024 | HPSS 1280024 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1993 | 108.1 | 48.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 108.1 |  | 0 | 0
1280065 | HPSS 1280065 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 11.62% | 11.62% | 1993 | 509.5 | 52.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 509.5 |  | 0 | 0
1280078 | HPSS 1280078 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1993 | 15 | 47.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
1280118 | HPSS 1280118 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1994 | 20 | 47.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1280142 | HPSS 1280142 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1994 | 198 | 48.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 198 |  | 0 | 0
1280255 | HPSS 1280255 | 600 | 3 |  | 1549 | 950 | 633 | UNKV |  | 633 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1995 | 117 | 47.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 117 |  | 0 | 0
1280349 | HPSS 1280349 | 600 | 3 |  | 1549 | 1000 | 666 | UNKV |  | 666 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1996 | 40 | 46.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
1280350 | HPSS 1280350 | 600 | 3 |  | 1549 | 1000 | 666 | UNKV |  | 666 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1996 | 66 | 46.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 66 |  | 0 | 0
1280379 | HPSS 1280379 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 11.62% | 11.62% | 1996 | 20 | 46.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1280381 | HPSS 1280381 | 600 | 3 |  | 1549 | 930 | 620 | UNKV |  | 620 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1997 | 6 | 45.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
1280433 | HPSS 1280433 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1997 | 81.2 | 45.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 81.2 |  | 0 | 0
1280747 | HPSS 1280747 | 600 | 3 |  | 1549 | 950 | 633 | UNKV |  | 633 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1999 | 19 | 44.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
1283703 | HPSS 1283703 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 7 | 48.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
1284775 | HPSS 1284775 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1990 | 10.3 | 49.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10.3 |  | 0 | 0
1284778 | HPSS 1284778 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 63.9 | 48.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 63.9 |  | 0 | 0
1284785 | HPSS 1284785 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1979 | 18 | 54.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
1284795 | HPSS 1284795 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1990 | 49.2 | 49.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.2 |  | 0 | 0
1284796 | HPSS 1284796 | 600 | 3 |  | 1549 | 1000 | 666 | UNKV |  | 666 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 2007 | 43.8 | 40.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43.8 |  | 0 | 0
1289520 | HPSS 1289520 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1973 | 48 | 57.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48 |  | 0 | 0
1289523 | HPSS 1289523 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1992 | 64 | 48.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 64 |  | 0 | 0
1289660 | HPSS 1289660 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1972 | 183 | 59.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 183 |  | 0 | 0
1289661 | HPSS 1289661 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1988 | 16 | 50.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
1289662 | HPSS 1289662 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 310 | 49.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 310 |  | 0 | 0
1289663 | HPSS 1289663 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1993 | 21.8 | 47.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21.8 |  | 0 | 0
1289670 | HPSS 1289670 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1981 | 9.5 | 53.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9.5 |  | 0 | 0
1289677 | HPSS 1289677 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 8 | 48.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
1289680 | HPSS 1289680 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1972 | 23.9 | 58.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.9 |  | 0 | 0
1289682 | HPSS 1289682 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 2006 | 22 | 41.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
1289697 | HPSS 1289697 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1989 | 8 | 49.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
1289701 | HPSS 1289702 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 98.9 | 48.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 98.9 |  | 0 | 0
1326579 | HPSS 1326579 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1990 | 16 | 49.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
1326925 | HPSS 1326925 | 600 | 3 |  | 1549 | 950 | 633 | UNKV |  | 633 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1997 | 36.1 | 45.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36.1 |  | 0 | 0
988700202 | HPSS 988700202 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1986 | 34.1 | 51.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.1 |  | 0 | 0
1988700203 | HPSS 1988700203 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1974 | 88.8 | 57.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 88.8 |  | 0 | 0
2055900967 | HPSS 2055900967 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1996 | 22 | 46.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
4098700315 | HPSS 4098700315 | 600 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 11.62% | NA | 1991 | 11.8 | 48.62 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11.8 |  | 0 | 0
196866 | 4" North Lynden H.P. Line | 400 | 3 |  | 1052 | 645 | 430 | 250 |  | 250 |  |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 11.40% | 7.30% | 2013 | 404.7 | 34.4 | Expose/Verify/Replace | 2024-2028 | 1 | 1 | 0 | 404.7 |  | 0 | 0
20564 | Bellingham H.P. Distribution System | 150 | 4 |  | 399 | 225 | 150 | 250 |  | 150 | X |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 11.01% | 11.01% | 1972 | 320.8 | 60.51 | 116 Segment, Replace | 2019 | 1 | 1 | 0 | 320.8 |  | 0 | 0
42515 | 005-O-009 | 780 | 3 |  | 2260 | 850 | 566 | NA |  | 566 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 10.35% | NA | 1993 | 20 | 47.35 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
11480 | Bellingham H.P. Distribution System | 150 | 4 |  | 334 | 0 | 0 | 250 |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 9.83% | 14.34% | 1956 | 1955.4 | 107.84 | 116 Segment, Replace | 2019 | 1 | 0 | 1955.4 | 0 |  | 0 | 0
685 | Service Stub, Georgia Pacific | 250 | 4 |  | 836 | 600 | 1 | 250 |  | 1 |  |  | UNVALID | 8.625 | 0.322 | 35000 | 0.8 | NO | NO | YES | 9.57% | 9.57% | 2001 | 708 | 44.57 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 708 |  | 0 | 0
60442 | 005-V-164 | 250 | 3 |  | 1045 | 750 | 500 | 1440 |  | 500 | X | Service | VALID | 8.625 | 0.322 | 35000 | 0.8 | NO | NO | YES | 9.57% | 9.57% | 2001 | 0 | 32.57 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
1158815 | HPSS 1158815 | 380 | 3 |  | 1193 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 9.55% | NA | 1998 | 145.5 | 44.05 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 145.5 |  | 0 | 0
1925083874 | HPSS 1925083874 | 380 | 3 |  | 1193 | 380 | 253 | UNKV |  | 253 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 9.55% | NA | 2014 | 21.6 | 35.05 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 21.6 |  | 0 | 0
10C1315 | Bellingham H.P. Distribution System | 150 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 9.01% | 9.01% | 1958 | 931.1 | 89.51 | 116 Segment, Replace | 2019 | 1 | 0 | 931.1 | 0 |  | 0 | 0
10C1559 | Bellingham H.P. Distribution System | 150 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 9.01% | NA | 1958 | 421.8 | 85.51 | 116 Segment, Replace | 2019 | 1 | 0 | 421.8 | 0 |  | 0 | 0
10C3298 | Bellingham H.P. Distribution System | 150 | 4 |  | 399 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 42000 | 0.8 | YES | YES | YES | 9.01% | 9.01% | 1960 | 1083.6 | 92.01 | 116 Segment, Replace | 2019 | 1 | 0 | 1083.6 | 0 |  | 0 | 0
10C8241 | Bellingham H.P. Distribution System | 150 | 4 |  | 399 | 0 | 0 | 250 |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 9.01% | 9.01% | 1964 | 2374 | 88.01 | 116 Segment, Replace | 2019 | 1 | 0 | 2374 | 0 |  | 0 | 0
1570 | Inlet 005-R-135 | 150 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 9.01% | NA | 1956 | 32.1 | 86.51 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 32.1 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
16252 | Inlet 005-R-004 | 150 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 9.01% | NA | 1970 | 14.5 | 72.51 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 14.5 | 0 |  | 0 | 0
1380 | Inlet 005-R-128 | 150 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 9.01% | NA | 1957 | 102.2 | 86.51 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 102.2 | 0 |  | 0 | 0
47810 | Inlet 005-R-126 | 400 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 1996 | 29.5 | 34.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 29.5 |  | 0 | 0
27205 | 4" South Everson H.P. Line | 250 | 3 |  | 499 | 450 | 300 | 720 |  | 300 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1982 | 14921.5 | 71.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 14921.5 | 1 | 0 | 14921.5 |  | 1
33194 | 4" Blaine H.P. Line | 250 | 3 |  | 499 | 375 | 250 | 400 |  | 250 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1986 | 20920.6 | 69.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20920.6 | 1 | 0 | 20920.6 |  | 1
43171 | 12", 16" & 4" Squalicum H.P. Line | 250 | 4 |  | 701 | 710 | 473 | 250 |  | 250 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1992 | 728 | 43.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 728 | 1 | 0 | 728 |  | 1
44277 | 4" South Lynden H.P. Line | 250 | 3 |  | 877 | 675 | 450 | 720 |  | 450 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 8.55% | 1993 | 7978.5 | 45.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7978.5 | 1 | 0 | 7978.5 |  | 1
51333 | 4" South Lynden H.P. Line | 250 | 3 |  | 877 | 720 | 480 | NA |  | 480 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 8.55% | NA | 1996 | 5600 | 44.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5600 | 1 | 0 | 5600 |  | 1
59402 | 4" Squalicum H.P. Line | 250 | 4 |  | 701 | 730 | 486 | 720 |  | 486 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 2002 | 11545.7 | 48.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 11545.7 | 1 | 0 | 11545.7 |  | 1
164230 | 4" South Lynden H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 8.55% | NA | 2009 | 2.9 | 27.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2.9 | 1 | 0 | 2.9 |  | 1
206197 | 4" South Lynden H.P. Line | 250 | 3 |  | 499 | 660 | 440 | 250 |  | 250 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 2013 | 32.1 | 41.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 32.1 | 1 | 0 | 32.1 |  | 1
28563 | 4" Blaine H.P. Line | 250 | 3 |  | 877 | 900 | 600 | NA |  | 600 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 8.55% | NA | 1980 | 1391.4 | 49.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1391.4 | 1 | 0 | 1391.4 |  | 1
33763 | Outlet 005-R-079 | 250 | 3 |  | 877 | 900 | 600 | NA |  | 600 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1986 | 6.8 | 39.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6.8 | 1 | 0 | 6.8 |  | 1
44414 | 4" South Everson H.P. Line | 250 | 3 |  | 499 | 760 | 506 | UNKV |  | 499 | X | X | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 8.55% | 15.02% | 1994 | 2131.9 | 58.02 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2131.9 |  | 0 | 0
23013 | 4" South Lynden H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 8.03% | 1974 | 726.6 | 54.05 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 726.6 |  | 0 | 0
A0078424 | Inlet 005-R-154 | 380 | 3 |  | 933 | 600 | 400 | 250 |  | 250 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.37% | 12.21% | 2005 | 15.8 | 42.21 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 15.8 |  | 0 | 0
12207 | Inlet 005-R-024 | 380 | 3 |  | 1361 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NA | NA | 8.37% | NA | 1967 | 10 | 55.87 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 10 | 0 |  | 0 | 0
25324 | Main Stub (005-R-062) | 380 | 3 |  | 933 | 600 | 1 | 1440 |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.37% | 12.21% | 1977 | 152.5 | 62.21 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 152.5 |  | 0 | 0
22593 | Main Stub (005-R-049) | 380 | 3 |  | 1193 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.37% | 9.55% | 1974 | 25.9 | 70.05 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 25.9 |  | 0 | 0
A0084192 | Inlet 005-R-161 | 380 | 3 |  | 1361 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.37% | 8.37% | 2008 | 173.1 | 48.87 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 173.1 |  | 0 | 0
56741 | Inlet 005-R-020 | 380 | 3 |  | 1193 | 540 | 360 | 720 |  | 360 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.37% | 9.55% | 1999 | 48.8 | 52.55 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 48.8 |  | 0 | 0
14089 | Inlet 005-R-038 | 380 | 3 |  | 1361 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.37% | NA | 1968 | 7.6 | 69.87 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 7.6 | 0 |  | 0 | 0
14774 | Inlet 005-R-023 | 380 | 3 |  | 1361 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.37% | NA | 1968 | 12.5 | 69.87 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 12.5 | 0 |  | 0 | 0
39699 | Inlet 005-R-154 | 380 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.37% | 8.37% | 1991 | 25 | 36.37 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
40741 | Inlet 005-R-101 | 380 | 3 |  | 1361 | 600 | 400 | NA |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.37% | NA | 1991 | 2.8 | 36.37 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2.8 | 1 | 0 | 2.8 |  | 1
44840 | Inlet 005-R-115 | 380 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.37% | 8.37% | 1993 | 29 | 35.37 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 29 | 1 | 0 | 29 |  | 1
45980 | Inlet 005-R-122 | 380 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.37% | 8.37% | 1994 | 25.5 | 34.87 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25.5 | 1 | 0 | 25.5 |  | 1
A0066250 | Inlet 005-R-145 | 380 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.37% | NA | 2001 | 26.6 | 31.37 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 26.6 | 1 | 0 | 26.6 |  | 1
56324 | 8" Central Whatcom H.P. Line | 380 | 3 |  | 1361 | 600 | 400 | UNKV |  | 400 | X | X | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NA | NA | 8.37% | NA | 1999 | 16.5 | 32.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.5 |  | 0 | 0
34139 | Inlet 005-R-084 | 380 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.37% | 8.37% | 1986 | 20.6 | 38.87 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 20.6 |  | 0 | 0
40763 | Inlet 005-R-101 | 380 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.37% | NA | 1991 | 29.8 | 36.37 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 29.8 |  | 0 | 0
58365 | Inlet 005-R-019 | 380 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.37% | 8.37% | 2000 | 67.9 | 31.87 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 67.9 |  | 0 | 0
16C7000 | 2" Nooksack H.P. Distribution System | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1963 | 731.9 | 83.53 | 116 Segment, Replace | 2020 | 1 | 0 | 731.9 | 0 |  | 0 | 0
59466 | Inlet 005-R-140 | 250 | 4 |  | 746 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 8.03% | 2001 | 167 | 58.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 167 |  | 0 | 0
A0066236 | 005-O-010 | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 1961 | 0 | 80.53 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 0 | 0 |  | 0 | 0
1402955 | Inlet 005-R-072 | 250 | 3 |  | 933 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1981 | 12 | 50.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 12 |  | 0 | 0
1370 | Service Stub | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1981 | 12 | 65.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 12 |  | 0 | 0
840 | Inlet 005-R-058 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1963 | 419 | 79.53 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 419 | 0 |  | 0 | 0
17C4065 | Main Stub | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1971 | 20.7 | 70.03 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 20.7 |  | 0 | 0
2227 | HPSS 2227 | 250 | 3 |  | 933 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1980 | 20 | 45.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1291800 | Inlet 005-R-104 | 250 | 3 |  | 933 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1980 | 22 | 45.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
1326991 | HPSS 1326991 | 600 | 3 |  | 2260 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 7.96% | NA | 2000 | 14.1 | 31.46 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14.1 |  | 0 | 0
25893 | Inlet 005-R-063 | 600 | 3 |  | 2260 | 900 | 600 | 1200 |  | 600 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NO | YES | 7.96% | 7.96% | 1978 | 7.9 | 42.46 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 7.9 |  | 0 | 0
1312100 | HPSS 1312100 | 400 | 3 |  | 1549 | 470 | 313 | UNKV |  | 313 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1979 | 25.1 | 50.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 25.1 |  | 0 | 0
1319145 | HPSS 1319145 | 400 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1995 | 186.7 | 43.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 186.7 |  | 0 | 0
1312095 | HPSS 1312095 | 400 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1987 | 25.8 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25.8 |  | 0 | 0
1318881 | HPSS 1318881 | 400 | 3 |  | 1549 | 625 | 416 | UNKV |  | 416 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1992 | 34.9 | 39.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.9 |  | 0 | 0
1319406 | HPSS 1319406 | 400 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1997 | 39.7 | 36.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39.7 |  | 0 | 0
1319677 | HPSS 1319677 | 400 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2000 | 25 | 35.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
10C9683 | Bellingham H.P. Distribution System | 150 | 4 |  | 635 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 7.55% | 6.60% | 1956 | 940.3 | 92.05 | 116 Segment, Replace | 2019 | 1 | 0 | 940.3 | 0 |  | 0 | 0
33211 | 4" & 6" Bay Road H.P. Line | 150 | 3 |  | 794 | 375 | 250 | 720 |  | 250 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 7.55% | 5.07% | 1986 | 6048.9 | 52.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6048.9 | 1 | 0 | 6048.9 |  | 1
18048 | Bellingham H.P. Distribution System | 150 | 4 |  | 635 | 418 | 278 | UNKV |  | 278 | X | X | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | NO | YES | 7.55% | 5.07% | 1971 | 3150.1 | 55.05 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 3150.1 |  | 0 | 0
1158689 | HPSS 1158689 | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1993 | 94.1 | 43.36 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 94.1 |  | 0 | 0
1158713 | HPSS 1158713 | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 1994 | 113.2 | 43.86 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 113.2 |  | 0 | 0
1158732 | HPSS 1158731 | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 295.1 | 43.86 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 295.1 |  | 0 | 0
1158789 | HPSS 1158789 | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1996 | 46 | 41.86 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
5641700544 | HPSS 5641700544 | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 2007 | 61.2 | 36.36 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 61.2 |  | 0 | 0
1158918 | HPSS 1158918 | 380 | 3 |  | 1549 | 600 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 2004 | 20.3 | 37.86 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20.3 |  | 0 | 0
886447 | Service Stub | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 2001 | 64.8 | 39.36 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 64.8 |  | 0 | 0
886484 | HPSS 886484 | 380 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 134.9 | 43.86 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 134.9 |  | 0 | 0
1110385 | HPSS 1110385 | 380 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1977 | 50 | 61.36 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 50 |  | 0 | 0
1117254 | HPSS 1117648 | 380 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 1973 | 34 | 63.36 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 34 |  | 0 | 0
1158875 | HPSS 1158875 | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 2002 | 31.3 | 38.86 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 31.3 |  | 0 | 0
1275450 | HPSS 1275450 | 380 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1963 | 90 | 62.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 90 | 0 |  | 0 | 0
1281740 | HPSS 1281740 | 380 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1963 | 65.5 | 62.86 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 65.5 | 0 |  | 0 | 0
1281745 | HPSS 1281745 | 380 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1963 | 64.2 | 62.86 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 64.2 | 0 |  | 0 | 0
1281790 | HPSS 1281790 | 380 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1970 | 13 | 55.86 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 13 | 0 |  | 0 | 0
1281890 | HPSS 1281890 | 380 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1957 | 1 | 68.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 1 | 0 |  | 0 | 0
883395 | HPSS 883395 | 380 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 1968 | 136.3 | 58.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 136.3 | 0 |  | 0 | 0
883570 | HPSS 883570 | 380 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1960 | 55.6 | 65.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 55.6 | 0 |  | 0 | 0
883388 | HPSS 883388 | 380 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1967 | 5 | 73.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 5 | 0 |  | 0 | 0
883568 | HPSS 883568 | 380 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1965 | 45.9 | 75.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 45.9 | 0 |  | 0 | 0
883572 | HPSS 883572 | 380 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1970 | 21.7 | 80.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 21.7 | 0 |  | 0 | 0
883573 | HPSS 883573 | 380 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1970 | 18.7 | 70.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 18.7 | 0 |  | 0 | 0
454800372 | HPSS 454800372 | 380 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1957 | 7 | 68.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 7 | 0 |  | 0 | 0
5733800397 | HPSS 5733800397 | 380 | 3 |  | 1549 | 380 | 253 | UNKV |  | 253 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1997 | 109.8 | 42.36 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 109.8 |  | 0 | 0
A0070652 | Inlet 005-R-164 | 380 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1992 | 104 | 44.86 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 104 |  | 0 | 0
190 | Service to 3901 Unick Rd | 380 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 166 | 58.86 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 166 |  | 0 | 0
1281735 | HPSS 1281735 | 380 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1979 | 1 | 50.36 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 1 |  | 0 | 0
1490125 (Stub) | Service Stub | 380 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1986 | 0 | 46.86 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 0 |  | 0 | 0
1281860 | HPSS 1281860 | 380 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1983 | 3 | 63.36 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 3 |  | 0 | 0
883420 | HPSS 883420 | 380 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1961 | 0 | 79.86 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 0 | 0 |  | 0 | 0
883390 | HPSS 883390 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1997 | 22 | 36.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
883566 | HPSS 883566 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 1997 | 79 | 36.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 79 |  | 0 | 0
883569 | HPSS 883569 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1985 | 39.2 | 42.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39.2 |  | 0 | 0
883571 | HPSS 883571 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1974 | 43.8 | 47.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43.8 |  | 0 | 0
884006 | HPSS 884006 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1989 | 48 | 40.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48 |  | 0 | 0
884008 | HPSS 884008 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1985 | 43 | 42.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
884300 | HPSS 884300 | 380 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1985 | 10 | 42.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
884700 | HPSS 884700 | 380 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1986 | 8.2 | 41.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8.2 |  | 0 | 0
886358 | HPSS 886358 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1992 | 27 | 38.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 27 |  | 0 | 0
886407 | HPSS 886407 | 380 | 3 |  | 1549 | 875 | 583 | UNKV |  | 583 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1993 | 144.3 | 39.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 144.3 |  | 0 | 0
886614 | HPSS 886614 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1996 | 112.3 | 37.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 112.3 |  | 0 | 0
1110384 | HPSS 1110384 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1973 | 24 | 48.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24 |  | 0 | 0
1110388 | HPSS 1110388 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1973 | 10 | 48.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
1111243 | HPSS 1111243 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1983 | 26 | 43.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26 |  | 0 | 0
1117305 | HPSS 1117305 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 1992 | 174.6 | 39.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 174.6 |  | 0 | 0
1152100 | HPSS 1152100 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 55.5 | 37.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.5 |  | 0 | 0
1158541 | HPSS 1158541 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1990 | 20 | 39.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1158692 | HPSS 1158692 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1993 | 197.7 | 39.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 197.7 |  | 0 | 0
1158694 | HPSS 1158694 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1993 | 83.6 | 38.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 83.6 |  | 0 | 0
1158696 | HPSS 1158696 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 121.4 | 38.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 121.4 |  | 0 | 0
1158699 | HPSS 1158699 | 380 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 177.8 | 38.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 177.8 |  | 0 | 0
1158706 | HPSS 1158706 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 58 | 37.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
1158708 | HPSS 1158708 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1994 | 62.7 | 37.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 62.7 |  | 0 | 0
1158715 | HPSS 1158715 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.36% | 7.36% | 1994 | 197.9 | 38.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 197.9 |  | 0 | 0
1158739 | HPSS 1158739 | 380 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1995 | 99 | 37.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 99 |  | 0 | 0
1158750 | HPSS 1158750 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1995 | 112.6 | 38.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 112.6 |  | 0 | 0
1158752 | HPSS 1158752 | 380 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1996 | 136.8 | 37.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 136.8 |  | 0 | 0
1158770 | HPSS 1158770 | 380 | 3 |  | 1549 | 790 | 526 | UNKV |  | 526 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1996 | 15.5 | 36.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15.5 |  | 0 | 0
1158786 | HPSS 1158786 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1997 | 46.9 | 36.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46.9 |  | 0 | 0
1158791 | HPSS 1158791 | 380 | 3 |  | 1549 | 950 | 633 | UNKV |  | 633 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1997 | 47.1 | 36.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47.1 |  | 0 | 0
1158834 | HPSS 1158834 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1999 | 40 | 35.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
1275390 | HPSS 1275390 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1992 | 201 | 39.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 201 |  | 0 | 0
1275395 | HPSS 1275395 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1984 | 32.4 | 42.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 32.4 |  | 0 | 0
1280032 | HPSS 1280032 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1993 | 16.6 | 38.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.6 |  | 0 | 0
1280533 | HPSS 1280533 | 380 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1998 | 179 | 36.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 179 |  | 0 | 0
1280651 | HPSS 1280651 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1998 | 21 | 35.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
1280912 | HPSS 1280912 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 2000 | 13 | 34.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
1281732 | HPSS 1281732 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1988 | 7 | 40.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
1281738 | HPSS 1281738 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1989 | 115 | 41.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 115 |  | 0 | 0
1281760 | HPSS 1281760 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1993 | 72.7 | 38.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 72.7 |  | 0 | 0
2454800374 | HPSS 2454800374 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1992 | 86 | 38.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 86 |  | 0 | 0
5531700569 | HPSS 5531700569 | 380 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1999 | 22 | 35.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
7683800794 | HPSS 7683800794 | 380 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 2001 | 27 | 34.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 27 |  | 0 | 0
9349400969 | HPSS 9349400969 | 380 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.36% | NA | 1993 | 141 | 39.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 141 |  | 0 | 0
177227 | 4" West Ferndale H.P. Line | 250 | 3 |  | 1052 | 840 | 560 | 1440 |  | 560 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 7.12% | 6.78% | 2012 | 7815.7 | 34.62 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7815.7 | 1 | 0 | 7815.7 |  | 1
196032 | 005-R-169 | 250 | 3 |  | 1052 | 840 | 560 | 720 |  | 560 | X | X | VALID | 6.625 | 0.28 | 52000 | 0.8 | NO | NO | YES | 7.12% | 6.78% | 2012 | 51.5 | 24.62 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 51.5 | 1 | 0 | 51.5 |  | 1
196033 | Inlet 005-R-170 | 250 | 3 |  | 1052 | 840 | 560 | 720 |  | 560 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 7.12% | 4.56% | 2012 | 42.4 | 24.62 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 42.4 | 1 | 0 | 42.4 |  | 1
53163 | Inlet 005-R-131 | 250 | 3 |  | 1106 | 600 | 400 | NA |  | 400 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NA | NA | 6.78% | NA | 1997 | 5 | 31.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5 | 1 | 0 | 5 |  | 1
AA000801 | 005-V-165 | 250 | 3 |  | 1106 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 6.78% | 6.78% | 2002 | 0 | 29.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
192833 | Inlet 005-R-064 | 250 | 3 |  | 1193 | 750 | 1 | 740 |  | 1 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | YES | YES | 6.28% | 6.28% | 2012 | 1 | 32.78 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 1 |  | 0 | 0
1471600263 | HPSS 1471600263 | 250 | 4 |  | 954 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1992 | 18 | 44.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
5350662606 | HPSS 5350662606 | 250 | 3 |  | 1193 | 95 | 63 | UNKV |  | 63 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2017 | 26 | 30.28 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 26 |  | 0 | 0
639400902 | HPSS 639400902 | 250 | 3 |  | 1193 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2015 | 29.1 | 26.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29.1 |  | 0 | 0
3709809524 | HPSS 3709809524 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2016 | 20.5 | 25.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.5 |  | 0 | 0
8893900683 | HPSS 8893900683 | 250 | 3 |  | 1193 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1989 | 115 | 40.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 115 |  | 0 | 0
8974900380 | HPSS 8974900380 | 250 | 3 |  | 1193 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1972 | 57 | 47.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57 |  | 0 | 0
9448900586 | HPSS 9448900586 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2015 | 149 | 27.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 149 |  | 0 | 0
178608 | Bellingham H.P. Distribution System | 150 | 4 |  | 760 | 400 | 266 | 960 |  | 266 | X | X | VALID | 10.75 | 0.25 | 52000 | 0.8 | NO | NO | YES | 6.20% | 6.31% | 2010 | 500.6 | 31.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 500.6 | 1 | 0 | 500.6 |  | 1
210696 | Bellingham H.P. Distribution System | 150 | 3 |  | 933 | 660 | 440 | UNKV |  | 440 | X | X | UNVALID | 10.75 | 0.25 | 52000 | 0.8 | YES | YES | YES | 6.20% | 6.31% | 2014 | 973.3 | 31.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 973.3 |  | 0 | 0
217117 | Bellingham H.P. Distribution System | 150 | 3 |  | 950 | 620 | 413 | UNKV |  | 413 | X | X | UNVALID | 10.75 | 0.25 | 52000 | 0.8 | YES | YES | YES | 6.20% | 6.31% | 2014 | 15.3 | 26.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15.3 |  | 0 | 0
1374790 | Service Stub | 250 | 3 |  | 1214 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 6.18% | NA | 1974 | 100.6 | 47.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 100.6 |  | 0 | 0
34405 - 170 | 4" South Sumas H.P. Line | 170 | 3 |  | 877 | 375 | 250 | 250 |  | 250 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.81% | 4.61% | 1987 | 6566.5 | 45.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6566.5 | 1 | 0 | 6566.5 |  | 1
40143 | 4" South Sumas H.P. Line | 170 | 3 |  | 877 | 640 | 426 | 720 |  | 426 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.81% | 4.61% | 1987 | 478.3 | 40.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 478.3 |  | 0 | 0
A0070915 | Inlet 005-R-141 | 150 | 3 |  | 665 | 425 | 283 | 720 |  | 283 | X |  | UNVALID | 6.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 5.68% | 9.01% | 2004 | 24.2 | 34.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 24.2 |  | 0 | 0
7766800130 | Service to 4100 W Unick Rd. | 380 | 3 |  | 933 | 620 | 413 | 720 |  | 413 | X | Service | VALID | 2.375 | 0.154 | 52000 | 0.6 | NO | YES | YES | 5.63% | 12.21% | 2016 | 0 | 36.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
20048 | 2" Nooksack H.P. Distribution System | 250 | 3 |  | 1361 | 300 | 200 | NA |  | 200 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1972 | 740.2 | 53.01 | 116 Segment, Downrate | 2022 | 1 | 1 | 0 | 740.2 |  | 0 | 0
20519 | 2" Nooksack H.P. Distribution System | 250 | 3 |  | 1361 | 300 | 200 | NA |  | 200 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1972 | 493 | 49.01 | 116 Segment, Downrate | 2022 | 1 | 1 | 0 | 493 |  | 0 | 0
27342 | Inlet 005-R-070 | 250 | 3 |  | 1106 | 100 | 1 | 400 |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 6.78% | 1980 | 99.5 | 45.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 99.5 |  | 0 | 0
34853 | Inlet 005-R-091 | 250 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1987 | 115.4 | 41.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 115.4 |  | 0 | 0
41675 | Inlet 005-R-105 | 250 | 3 |  | 1361 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 5.39% | 1992 | 69.9 | 57.01 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 69.9 |  | 0 | 0
A0078667 | Inlet 005-R-156 | 250 | 3 |  | 1361 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NO | YES | 5.51% | 5.51% | 2005 | 52 | 31.51 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 52 |  | 0 | 0
29329 | 2" Nooksack H.P. Distribution System | 250 | 3 |  | 1361 | 375 | 250 | NA |  | 250 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1981 | 2814.3 | 46.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2814.3 | 1 | 0 | 2814.3 |  | 1
33810 | 4" Blaine H.P. Line (Loomis Trail Rd) | 250 | 3 |  | 933 | 375 | 250 | 1440 |  | 250 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1986 | 388.9 | 43.53 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 388.9 | 1 | 0 | 388.9 |  | 1
44262 | 2" Nooksack H.P. Distribution System | 250 | 3 |  | 1193 | 600 | 400 | 1440 |  | 400 | X | NA | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 6.28% | 1956 | 283.9 | 64.78 | Accept Most Stringent Criteria | -- | 1 | 0 | 283.9 | 0 | 1 | 283.9 | 0 | 1
46250 | 4" South Lynden H.P. Line | 250 | 3 |  | 933 | 425 | 283 | 1440 |  | 283 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1993 | 128.1 | 40.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 128.1 | 1 | 0 | 128.1 |  | 1
31234 | Inlet 005-R-036 | 250 | 3 |  | 1361 | 900 | 600 | 250 |  | 250 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1984 | 18.7 | 37.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 18.7 | 1 | 0 | 18.7 |  | 1
37648 | Inlet 005-R-097 | 250 | 3 |  | 1361 | 700 | 466 | 1440 |  | 466 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1990 | 8.5 | 34.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 8.5 | 1 | 0 | 8.5 |  | 1
41166 | Inlet 005-R-111 | 250 | 3 |  | 1106 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 6.78% | 1993 | 17.8 | 33.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 17.8 | 1 | 0 | 17.8 |  | 1
33811 | Inlet 005-R-081 | 250 | 3 |  | 1361 | 375 | 250 | 1440 |  | 250 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1986 | 82.7 | 36.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 82.7 |  | 0 | 0
35255 | Inlet 005-R-091 | 250 | 3 |  | 1361 | 400 | 266 | NA |  | 266 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1988 | 16.9 | 35.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 16.9 |  | 0 | 0
A0066734 | Inlet 005-R-147 | 250 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 2003 | 39.1 | 34.03 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 39.1 |  | 0 | 0
A0066749 | Inlet 005-R-148 | 250 | 4 |  | 1089 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2002 | 34.2 | 30.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 34.2 |  | 0 | 0
AA000777 | Inlet 005-R-146 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2001 | 11.7 | 28.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 11.7 |  | 0 | 0
1437666 | Service Stub | 170 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 5.46% | 5.46% | 2002 | 1 | 51.96 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 1 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1437704 | HPSS 1437704 | 170 | 3 |  | 933 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 5.46% | NA | 2008 | 17.7 | 28.96 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17.7 |  | 0 | 0
54421 | Inlet 005-R-135 | 155 | 3 |  | 877 | 305 | 203 | 720 |  | 203 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 5.30% | NA | 1998 | 38.6 | 29.8 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 38.6 | 1 | 0 | 38.6 |  | 1
211165 | Bellingham H.P. Distribution System | 155 | 3 |  | 641 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 3.5 | 0.216 | 24000 | 0.6 | YES | YES | YES | 5.23% | 7.24% | 1955 | 87.4 | 85.74 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 87.4 | 0 |  | 0 | 0
20752 | Bellingham H.P. Distribution System | 150 | 4 |  | 701 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.13% | 4.07% | 1972 | 48.8 | 49.63 | 116 Segment, Replace | 2019 | 1 | 1 | 0 | 48.8 |  | 0 | 0
21298 | Bellingham H.P. Distribution System | 150 | 4 |  | 701 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.13% | 4.07% | 1973 | 123 | 65.13 | 116 Segment, Replace | 2019 | 1 | 1 | 0 | 123 |  | 0 | 0
39957 | Bellingham H.P. Distribution System | 150 | 3 |  | 499 | 300 | 200 | 200 |  | 200 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.13% | 9.01% | 1991 | 281.6 | 42.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 281.6 | 1 | 0 | 281.6 |  | 1
22344 | Bellingham H.P. Distribution System | 150 | 3 |  | 499 | 600 | 400 | UNKV |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 5.13% | 9.01% | 1973 | 164.8 | 51.01 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 164.8 |  | 0 | 0
59026 | Bellingham H.P. Distribution System | 150 | 4 |  | 399 | 310 | 206 | 275 |  | 206 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.13% | 9.01% | 2000 | 1269.2 | 46.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1269.2 |  | 0 | 0
19466 - 150 | 4" & 6" Bay Road H.P. Line | 150 | 3 |  | 877 | 750 | 500 | 275 |  | 275 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.13% | 4.07% | 1973 | 9326 | 52.13 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 9326 |  | 0 | 0
1117741 | HPSS 1117741 | 380 | 3 |  | 3766 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 1 | YES | NA | NA | 5.04% | NA | 2001 | 20.8 | 31.04 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20.8 |  | 0 | 0
211166 | Inlet 005-R-006 | 155 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 4.98% | 4.98% | 1957 | 6.7 | 66.48 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 6.7 | 0 |  | 0 | 0
14483 | 005-O-004, 005-R-032 | 155 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.98% | NA | 1968 | 14.3 | 55.48 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 14.3 | 0 |  | 0 | 0
1117530 | Service Stub | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 79 | 30.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 79 |  | 0 | 0
1370945 | HPSS 1370945 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1964 | 13 | 50.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 13 | 0 |  | 0 | 0
1371760 | HPSS 1371761 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1973 | 78 | 41.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 78 |  | 0 | 0
1371761 | HPSS 1371761 | 250 | 3 |  | 1549 | 90 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2006 | 42.9 | 25.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 42.9 |  | 0 | 0
1371900 | HPSS 1371900 | 250 | 3 |  | 1549 | 90 | 64 | UNKV |  | 64 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1969 | 47 | 45.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 47 | 0 |  | 0 | 0
1371910 | HPSS 1371910 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 3 | 53.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 3 | 0 |  | 0 | 0
1371920 | HPSS 1371920 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 3 | 53.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 3 | 0 |  | 0 | 0
1371930 | HPSS 1371930 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 3 | 53.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 3 | 0 |  | 0 | 0
1371940 | HPSS 1371940 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 3 | 53.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 3 | 0 |  | 0 | 0
1371960 | HPSS 1371960 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1962 | 37.4 | 52.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 37.4 | 0 |  | 0 | 0
1371970 | HPSS 1371970 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 4 | 53.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 4 | 0 |  | 0 | 0
1371980 | HPSS 1371980 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 40 | 53.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 40 | 0 |  | 0 | 0
1371990 | HPSS 1371990 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1969 | 11 | 45.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 11 | 0 |  | 0 | 0
1372000 | HPSS 1372000 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 10.3 | 46.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 10.3 | 0 |  | 0 | 0
1375800 | HPSS 1377644 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 201.2 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 201.2 |  | 0 | 0
1376210 | HPSS 1376210 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 49.3 | 33.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 49.3 |  | 0 | 0
1377764 | HPSS 1377764 | 250 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 97.1 | 31.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 97.1 |  | 0 | 0
1377823 | HPSS 1377823 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 36 | 30.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
1377828 | HPSS 1377828 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 58.6 | 30.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 58.6 |  | 0 | 0
1377844 | HPSS 1377844 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 8 | 29.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
1377896 | HPSS 1377896 | 250 | 3 |  | 1549 | 350 | 233 | UNKV |  | 233 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 29 | 29.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 29 |  | 0 | 0
1377913 | HPSS 1377913 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 20.1 | 28.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20.1 |  | 0 | 0
1377929 | HPSS 1377929 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 40.2 | 28.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40.2 |  | 0 | 0
1371500 | HPSS 1371500 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1969 | 8.3 | 45.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 8.3 | 0 |  | 0 | 0
1402930 | HPSS 1403949 | 250 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1972 | 73.3 | 42.34 | Addressed w/ 116 Segment | 2022 | 1 | 1 | 0 | 73.3 |  | 0 | 0
1402935 | HPSS 1402935 | 250 | 3 |  | 1549 | 350 | 233 | UNKV |  | 233 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 42 | 39.34 | Addressed w/ 116 Segment | 2022 | 1 | 1 | 0 | 42 |  | 0 | 0
1371510 | HPSS 1371510 | 250 | 3 |  | 1549 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2003 | 84.9 | 26.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 84.9 |  | 0 | 0
1371530 | HPSS 1371530 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1966 | 49.2 | 48.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 49.2 | 0 |  | 0 | 0
1498731 | HPSS 1498731 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 40 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
1371550 | HPSS 1371550 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1969 | 3 | 45.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 3 | 0 |  | 0 | 0
1371570 | HPSS 1371570 | 250 | 3 |  | 1549 | 30 | 21 | UNKV |  | 21 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 46.7 | 46.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 46.7 | 0 |  | 0 | 0
1371595 | HPSS 1371595 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1963 | 16.1 | 51.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 16.1 | 0 |  | 0 | 0
1371610 | HPSS 1371610 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1962 | 14.9 | 52.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 14.9 | 0 |  | 0 | 0
1371620 | HPSS 1371620 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1971 | 7 | 42.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 7 |  | 0 | 0
1371630 | HPSS 1371630 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1962 | 14.7 | 52.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 14.7 | 0 |  | 0 | 0
1371640 | HPSS 1371640 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1973 | 41.8 | 41.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 41.8 |  | 0 | 0
1371650 | HPSS 1371650 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1964 | 51.7 | 50.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 51.7 | 0 |  | 0 | 0
1371660 | HPSS 1371660 | 250 | 3 |  | 1549 | 95 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1964 | 30.9 | 50.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 30.9 | 0 |  | 0 | 0
1371700 | HPSS 1371700 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 2 | 46.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 2 | 0 |  | 0 | 0
1374252 | HPSS 1374252 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 81 | 38.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 81 |  | 0 | 0
1374540 | HPSS 1374540 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 39.8 | 53.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 39.8 | 0 |  | 0 | 0
1374545 | HPSS 1374545 | 250 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1966 | 38.9 | 48.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 38.9 | 0 |  | 0 | 0
1374570 | HPSS 1374570 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 32 | 53.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 32 | 0 |  | 0 | 0
1374590 | HPSS 1374590 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1964 | 20.3 | 50.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 20.3 | 0 |  | 0 | 0
1374650 | HPSS 1374650 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1963 | 40 | 51.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 40 | 0 |  | 0 | 0
1374660 | HPSS 1374660 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 39.4 | 53.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 39.4 | 0 |  | 0 | 0
1374680 | HPSS 1374680 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1967 | 18 | 47.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 18 | 0 |  | 0 | 0
1374700 | HPSS 1374700 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1965 | 25 | 49.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 25 | 0 |  | 0 | 0
1374720 | HPSS 1374720 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1963 | 48 | 51.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 48 | 0 |  | 0 | 0
1374740 | HPSS 1374740 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1963 | 21.9 | 51.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 21.9 | 0 |  | 0 | 0
1374760 | Service Stub | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 40 | 53.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 40 | 0 |  | 0 | 0
1374770 | Service Stub | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1963 | 40 | 51.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 40 | 0 |  | 0 | 0
1374860 | HPSS 1374860 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1971 | 51.2 | 42.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 51.2 |  | 0 | 0
1402800 | HPSS 1402800 | 250 | 3 |  | 1549 | 95 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1971 | 20 | 42.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 20 |  | 0 | 0
1402810 | HPSS 1402810 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1970 | 11.9 | 44.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 11.9 | 0 |  | 0 | 0
1402820 | HPSS 1402820 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1966 | 39.2 | 48.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 39.2 | 0 |  | 0 | 0
1402830 | HPSS 1402830 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1973 | 61.1 | 41.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 61.1 |  | 0 | 0
1402880 | HPSS 1402880 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1967 | 52 | 47.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 52 | 0 |  | 0 | 0
1402890 | HPSS 1402890 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1969 | 3 | 45.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 3 | 0 |  | 0 | 0
1402900 | HPSS 1402900 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1967 | 3 | 47.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 3 | 0 |  | 0 | 0
1402970 | HPSS 1402970 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 14 | 46.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 14 | 0 |  | 0 | 0
1402980 | HPSS 1402980 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 42.8 | 46.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 42.8 | 0 |  | 0 | 0
1403779 | HPSS 1403779 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 51 | 32.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 51 |  | 0 | 0
1403788 | HPSS 1403788 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 15 | 32.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 15 |  | 0 | 0
1403896 | HPSS 1403896 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1996 | 47.9 | 30.34 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 47.9 |  | 0 | 0
1371780 | HPSS 1371780 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 40 | 45.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
1371850 | HPSS 1371850 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 69.1 | 62.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 69.1 | 0 |  | 0 | 0
1377701 | HPSS 1377701 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1993 | 83.8 | 40.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 83.8 |  | 0 | 0
1402881 | HPSS 1402881 | 250 | 3 |  | 1549 | 620 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2004 | 19.5 | 26.34 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 19.5 |  | 0 | 0
1402901 | HPSS 1402901 | 250 | 3 |  | 1549 | 680 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 18 | 25.34 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 18 |  | 0 | 0
1373470 | HPSS 1373470 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1964 | 42.1 | 59.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 42.1 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
547620014 | Service Stub | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1986 | 19.2 | 44.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 19.2 |  | 0 | 0
1371590 | HPSS 1371590 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1963 | 16.2 | 60.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 16.2 | 0 |  | 0 | 0
1372820 | HPSS 1377620 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 36 | 62.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 36 | 0 |  | 0 | 0
1374675 | HPSS 1374675 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2007 | 113 | 34.84 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 113 |  | 0 | 0
1402680 | HPSS 1402680 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1961 | 12 | 62.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 12 | 0 |  | 0 | 0
1402860 | HPSS 1402860 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1965 | 35.1 | 58.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 35.1 | 0 |  | 0 | 0
837620061 | Service Stub | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 41.2 | 41.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 41.2 |  | 0 | 0
1402870 | HPSS 1402870 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1964 | 56.2 | 59.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 56.2 | 0 |  | 0 | 0
583900576 | Service Stub | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1974 | 49.9 | 50.34 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 49.9 |  | 0 | 0
1377620 | HPSS 1377620 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 99 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 99 |  | 0 | 0
1403908 | HPSS 1403908 | 250 | 3 |  | 1549 | 525 | 350 | UNKV |  | 350 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 57 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57 |  | 0 | 0
1372002 | HPSS 1372002 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 1 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1 |  | 0 | 0
995061 | HPSS 995061 | 250 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 17 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
995118 | HPSS 995118 | 250 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 18.9 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18.9 |  | 0 | 0
1280209 | HPSS 1280209 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 13 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
1285371 | HPSS 1285371 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2008 | 33.2 | 23.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 33.2 |  | 0 | 0
1289695 | HPSS 1289695 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 20 | 37.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1371600 | HPSS 1371600 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 79.3 | 37.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 79.3 |  | 0 | 0
1371632 | HPSS 1371632 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1987 | 60.1 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60.1 |  | 0 | 0
1371725 | HPSS 1371725 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 127.1 | 38.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 127.1 |  | 0 | 0
1371740 | HPSS 1371740 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 68 | 38.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 68 |  | 0 | 0
1371770 | HPSS 1371770 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1972 | 20 | 41.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1371997 | HPSS 1371997 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 68.8 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 68.8 |  | 0 | 0
1372040 | HPSS 1372040 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1986 | 54 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
1372365 | HPSS 1372365 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1988 | 103 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 103 |  | 0 | 0
1372785 | HPSS 1372785 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 83.1 | 37.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 83.1 |  | 0 | 0
1372810 | HPSS 1372810 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2003 | 69.8 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 69.8 |  | 0 | 0
1374240 | HPSS 1374240 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1975 | 7 | 39.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
1374560 | HPSS 1374560 | 250 | 3 |  | 1549 | 600 | 428 | UNKV |  | 428 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1965 | 22 | 48.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 22 | 0 |  | 0 | 0
1375102 | HPSS 1375102 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 39.8 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39.8 |  | 0 | 0
1375106 | HPSS 1375106 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 12 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
1375795 | HPSS 1375795 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 53.3 | 36.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 53.3 |  | 0 | 0
1376080 | HPSS 1376080 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 50 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
1376100 | HPSS 1376100 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 49.7 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.7 |  | 0 | 0
1376240 | HPSS 1376240 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 40.7 | 35.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.7 |  | 0 | 0
1377501 | HPSS 1377501 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 83.4 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 83.4 |  | 0 | 0
1377502 | HPSS 1377502 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 155.9 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 155.9 |  | 0 | 0
1377525 | HPSS 1377525 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 351.2 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 351.2 |  | 0 | 0
1377532 | HPSS 1377532 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 47 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
1377536 | HPSS 1377536 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 126 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 126 |  | 0 | 0
1377541 | HPSS 1377541 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 82 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 82 |  | 0 | 0
1377593 | HPSS 1377593 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 116 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 116 |  | 0 | 0
1377603 | HPSS 1377603 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 191 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 191 |  | 0 | 0
1377604 | HPSS 1377604 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 84.7 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 84.7 |  | 0 | 0
1377640 | HPSS 1377640 | 250 | 3 |  | 1549 | 675 | 450 | UNKV |  | 450 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 96 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 96 |  | 0 | 0
1377643 | HPSS 1377643 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 100.6 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 100.6 |  | 0 | 0
1377651 | HPSS 1377651 | 250 | 3 |  | 1549 | 675 | 450 | UNKV |  | 450 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 127.5 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 127.5 |  | 0 | 0
1377678 | HPSS 1377678 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 25 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
1377679 | HPSS 1377679 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 34.7 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.7 |  | 0 | 0
1377682 | HPSS 1377682 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 331.1 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 331.1 |  | 0 | 0
1377684 | HPSS 1377684 | 250 | 3 |  | 1549 | 675 | 450 | UNKV |  | 450 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 34.3 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.3 |  | 0 | 0
1377686 | HPSS 1377686 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 57.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.1 |  | 0 | 0
1377693 | HPSS 3814900835 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 339 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 339 |  | 0 | 0
1377694 | HPSS 1377694 | 250 | 3 |  | 1549 | 605 | 403 | UNKV |  | 403 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 58 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
1377699 | HPSS 1377699 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 157.4 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 157.4 |  | 0 | 0
1377729 | HPSS 1377729 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 90 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 90 |  | 0 | 0
1377737 | HPSS 1377737 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 122 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 122 |  | 0 | 0
1377789 | HPSS 1377789 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 324.2 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 324.2 |  | 0 | 0
1377797 | HPSS 1377797 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 330.4 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 330.4 |  | 0 | 0
1377798 | HPSS 1377798 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 306.8 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 306.8 |  | 0 | 0
1377816 | HPSS 1377816 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 128.1 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 128.1 |  | 0 | 0
1377837 | HPSS 1377837 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 10 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
1377901 | HPSS 1377901 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 60 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60 |  | 0 | 0
1377917 | HPSS 1377917 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 75.1 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 75.1 |  | 0 | 0
1377984 | HPSS 1377984 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 24.8 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24.8 |  | 0 | 0
1402838 | HPSS 1402838 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 36 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
1402952 | HPSS 1402952 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 38 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
1403000 | HPSS 1403000 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 29 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29 |  | 0 | 0
1403528 | HPSS 1403528 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 132.6 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 132.6 |  | 0 | 0
1403776 | HPSS 1403776 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 35 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
1403785 | HPSS 1403785 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 100 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 100 |  | 0 | 0
1403856 | HPSS 1403856 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 122.9 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 122.9 |  | 0 | 0
1403868 | HPSS 1403868 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 11 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
1403877 | HPSS 1403877 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 152 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 152 |  | 0 | 0
1403881 | HPSS 1403881 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 86.2 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 86.2 |  | 0 | 0
1403882 | HPSS 1403882 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 134.6 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 134.6 |  | 0 | 0
1403904 | HPSS 1403904 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 4 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4 |  | 0 | 0
1403951 | HPSS 1403951 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2000 | 36 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
1403978 | HPSS 1403978 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 10 | 24.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
1490120 | HPSS 1490120 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 25.6 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25.6 |  | 0 | 0
1490240 | HPSS 1490240 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 30 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
1490275 | HPSS 1490275 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 21 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
1490350 | HPSS 1490350 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 23.7 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.7 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1490375 | HPSS 1490375 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 49.4 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.4 |  | 0 | 0
1490388 | HPSS 1490388 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 25 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
1498675 | HPSS 1498675 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 41 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41 |  | 0 | 0
1498759 | HPSS 1498759 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 69.1 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 69.1 |  | 0 | 0
1498767 | HPSS 1498767 | 250 | 3 |  | 1549 | 550 | 366 | UNKV |  | 366 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 20.2 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.2 |  | 0 | 0
1498909 | HPSS 1498909 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 28 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 28 |  | 0 | 0
1499094 | HPSS 1499094 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 129 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 129 |  | 0 | 0
1499147 | HPSS 1499147 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 235.8 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 235.8 |  | 0 | 0
1499533 | HPSS 1499533 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 21.8 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21.8 |  | 0 | 0
1499546 | HPSS 1499546 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 55 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
1885900255 | HPSS 1885900255 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2001 | 77 | 26.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77 |  | 0 | 0
4746620017 | HPSS 4746620017 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 22 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
5246800916 | HPSS 5246800916 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 75.5 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 75.5 |  | 0 | 0
5666070880 | HPSS 5666070880 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 18 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
6309900016 | HPSS 6309900016 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 147.4 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 147.4 |  | 0 | 0
A0067838 | HPSS 1402850 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 40.1 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.1 |  | 0 | 0
1377641 | Service Stub | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 146.2 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 146.2 |  | 0 | 0
1377813 | HP Service Line (7180 Everson Goshen Rd #A) | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1996 | 358.8 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 358.8 |  | 0 | 0
1490125 | Inlet 005-R-098 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 12 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
25567 | Inlet 005-R-064 | 250 | 3 |  | 1549 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1978 | 45.1 | 38.34 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 45.1 |  | 0 | 0
10C4799 | Bellingham H.P. Distribution System | 150 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 4.82% | 4.82% | 1961 | 93.9 | 62.32 | 116 Segment, Replace | 2019 | 1 | 0 | 93.9 | 0 |  | 0 | 0
10C5321 | Bellingham H.P. Distribution System | 150 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 4.82% | 4.82% | 1963 | 1451.1 | 67.82 | 116 Segment, Replace | 2019 | 1 | 0 | 1451.1 | 0 |  | 0 | 0
10C9831 | Bellingham H.P. Distribution System | 150 | 3 |  | 257 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 4.82% | 17.50% | 1956 | 1273.4 | 109 | 116 Segment, Replace | 2019 | 1 | 0 | 1273.4 | 0 |  | 0 | 0
133 | HPSS 133 | 150 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.82% | NA | 2001 | 52 | 36.82 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
480 | Inlet 005-R-050 | 150 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 4.82% | NA | 1966 | 445 | 58.32 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 445 | 0 |  | 0 | 0
12841 | 005-O-005, 005-R-033 | 150 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.82% | NA | 1967 | 4.5 | 56.32 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 4.5 | 0 |  | 0 | 0
1253330 | Inlet 005-R-051 | 150 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 4.82% | NA | 1965 | 22 | 58.32 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 22 | 0 |  | 0 | 0
1253350 | HPSS 1253350 | 150 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 4.82% | 2.90% | 1979 | 41.5 | 47.82 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 41.5 |  | 0 | 0
PRE-CNG (005-O-006) | 005-O-006 | 150 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.82% | NA | 1967 | 18.5 | 56.32 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 18.5 | 0 |  | 0 | 0
30092 | Bellingham H.P. Distribution System | 150 | 3 |  | 933 | 225 | 150 | 250 |  | 150 | X | NA | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 4.82% | 4.82% | 1963 | 268.8 | 51.32 | Accept Most Stringent Criteria | -- | 1 | 0 | 268.8 | 0 | 1 | 268.8 | 0 | 1
33212 | Inlet 005-R-077 | 145 | 3 |  | 933 | 600 | 1 | NA |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.66% | NA | 1985 | 7.9 | 35.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 7.9 |  | 0 | 0
12081 | Inlet 005-R-057 | 250 | 3 |  | 1686 | 100 | 71 | 275 |  | 71 |  |  | UNVALID | 1.315 | 0.154 | 24000 | 0.6 | NO | YES | YES | 4.45% | 4.45% | 1966 | 22.2 | 47.95 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 22.2 | 0 |  | 0 | 0
185748 | Bellingham H.P. Distribution System | 150 | 3 |  | 1052 | 330 | 220 | 720 |  | 220 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 4.27% | 4.07% | 2011 | 128.2 | 22.27 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 128.2 | 1 | 0 | 128.2 |  | 1
213863 | Bellingham H.P. Distribution System | 150 | 4 |  | 842 | 300 | 200 | 720 |  | 200 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 4.27% | 4.07% | 2014 | 14.1 | 17.77 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 14.1 | 1 | 0 | 14.1 |  | 1
180093-OUT | Outlet 005-R-166 | 150 | 3 |  | 499 | 275 | 183 | NA |  | 183 | X | Service | VALID | 4.5 | 0.156 | 52000 | 0.6 | NO | YES | YES | 4.16% | 9.01% | 2010 | 41.8 | 31.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 41.8 | 1 | 0 | 41.8 |  | 1
4451600144 | HPSS 4451600144 | 150 | 3 |  | 1193 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.77% | NA | 1966 | 8 | 47.27 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 8 | 0 |  | 0 | 0
6219700501 | HPSS 6219700501 | 150 | 3 |  | 1193 | 30 | 21 | UNKV |  | 21 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.77% | NA | 1970 | 53 | 43.27 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 53 | 0 |  | 0 | 0
3430750404 | HPSS 3430750404 | 150 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 3.77% | 3.77% | 2016 | 50 | 18.27 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
6019700580 | HPSS 6019700580 | 150 | 4 |  | 954 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.77% | NA | 2015 | 19.1 | 20.77 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19.1 |  | 0 | 0
41939 | Inlet 005-R-108 | 170 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.75% | NA | 1992 | 31.1 | 26.25 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 31.1 | 1 | 0 | 31.1 |  | 1
1284985 | HPSS 1284985 | 150 | 3 |  | 1214 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 3.71% | NA | 1984 | 25 | 35.21 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
16675 | Inlet 005-R-030 | 250 | 3 |  | 2123 | 100 | 71 | 1440 |  | 71 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 3.53% | NA | 1969 | 65.5 | 40.03 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 65.5 | 0 |  | 0 | 0
8884900483 | HPSS 8884900483 | 250 | 3 |  | 1456 | 650 | 433 | 740 |  | 433 | X | Service | VALID | 1.315 | 0.133 | 24000 | 0.6 | NO | NA | NA | 5.15% | NA | 2017 | 79 | 24.15 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 79 | 1 | 0 | 79 |  | 1
224138 | Bellingham H.P. Distribution System | 150 | 4 |  | 884 | 300 | 200 | 720 |  | 200 | X | X | VALID | 4.5 | 0.188 | 52000 | 0.6 | NO | YES | YES | 3.45% | 5.07% | 2015 | 150.7 | 28.07 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 150.7 | 1 | 0 | 150.7 |  | 1
29722 | Inlet 005-R-006 | 155 | 3 |  | 933 | 250 | 1 | 400 |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.41% | 4.98% | 1982 | 21.6 | 37.48 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21.6 |  | 0 | 0
25046 | Main Stub (005-R-167) | 155 | 4 |  | 1089 | 0 | 0 | 1200 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.41% | 3.41% | 1977 | 59.7 | 49.41 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 59.7 |  | 0 | 0
48256 | Inlet 005-R-127 | 155 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.41% | NA | 1996 | 52.7 | 23.91 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 52.7 | 1 | 0 | 52.7 |  | 1
59030 | Inlet 005-R-009 | 155 | 4 |  | 1089 | 310 | 206 | 1440 |  | 206 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.41% | 3.41% | 2000 | 24.3 | 23.91 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 24.3 |  | 0 | 0
182371 | Inlet 005-R-159 | 250 | 3 |  | 2260 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 1994 | 54.2 | 25.82 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 54.2 |  | 0 | 0
230888 | Service Stub | 250 | 3 |  | 2260 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 3.32% | NA | 1963 | 43.7 | 54.82 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 43.7 | 0 |  | 0 | 0
1403945 | HPSS 1403945 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | YES | YES | 3.32% | 4.84% | 2000 | 74.7 | 37.34 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 74.7 |  | 0 | 0
219400 | HPSS 219400 | 250 | 3 |  | 2260 | 900 | 600 | UNKV |  | 600 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 1992 | 48.9 | 25.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48.9 |  | 0 | 0
A0072509 | Inlet 005-R-153 | 250 | 4 |  | 1808 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NO | YES | 3.32% | 2.62% | 2004 | 63 | 21.82 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 63 |  | 0 | 0
22537 | Main Stub | 150 | 3 |  | 933 | 100 | 66 | 250 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.30% | 4.82% | 1974 | 20.9 | 41.32 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20.9 |  | 0 | 0
22232 | Bellingham H.P. Distribution System | 150 | 3 |  | 1193 | 400 | 266 | 1440 |  | 266 | X | NA | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.30% | 3.77% | 1956 | 102.2 | 57.27 | Accept Most Stringent Criteria | -- | 1 | 0 | 102.2 | 0 | 1 | 102.2 | 0 | 1
21890 | Bellingham H.P. Distribution System | 150 | 3 |  | 1361 | 400 | 266 | 1200 |  | 266 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.30% | 3.30% | 1974 | 440.9 | 39.8 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 440.9 |  | 0 | 0
1247668 | HPSS 1437668 | 170 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1987 | 42 | 42.29 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
1247528 | HPSS 1247528 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.29% | 3.29% | 1991 | 427.3 | 31.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 427.3 |  | 0 | 0
1247529 | HPSS 1247529 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1991 | 102.1 | 31.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 102.1 |  | 0 | 0
1247505 | HPSS 1247505 | 170 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1992 | 104.1 | 30.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 104.1 |  | 0 | 0
1247506 | HPSS 1247506 | 170 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.29% | 3.29% | 1992 | 161 | 30.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 161 |  | 0 | 0
1247602 | HPSS 1247602 | 170 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1994 | 117.1 | 29.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 117.1 |  | 0 | 0
1437512 | HPSS 1437512 | 170 | 3 |  | 1549 | 475 | 316 | UNKV |  | 316 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.29% | 3.29% | 1990 | 127.1 | 31.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 127.1 |  | 0 | 0
1437513 | HPSS 1437513 | 170 | 3 |  | 1549 | 475 | 316 | UNKV |  | 316 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1990 | 69 | 30.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 69 |  | 0 | 0
1144091 | HPSS 1144091 | 155 | 3 |  | 1549 | 320 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 2004 | 56.3 | 24.5 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 56.3 |  | 0 | 0
886583 | HPSS 886583 | 155 | 3 |  | 1549 | 625 | 416 | UNKV |  | 416 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1995 | 190 | 29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 190 |  | 0 | 0
860121 | HPSS 860121 | 155 | 4 |  | 1239 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1997 | 19 | 29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
870350 | HPSS 870350 | 155 | 4 |  | 1239 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1989 | 100.4 | 34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 100.4 |  | 0 | 0
870385 | HPSS 870385 | 155 | 4 |  | 1239 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1974 | 55 | 40.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
870388 | HPSS 870388 | 155 | 4 |  | 1239 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1987 | 139.3 | 35 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 139.3 |  | 0 | 0
875007 | HPSS 875007 | 155 | 4 |  | 1239 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1990 | 29.1 | 32.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29.1 |  | 0 | 0
875078 | HPSS 875079 | 155 | 4 |  | 1239 | 350 | 233 | UNKV |  | 233 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1996 | 46 | 29.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
882203 | HPSS 882203 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1968 | 73.8 | 43.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 73.8 | 0 |  | 0 | 0
883061 | HPSS 883061 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1989 | 33.9 | 31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 33.9 |  | 0 | 0
886514 | HPSS 886514 | 155 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1994 | 54.3 | 28.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54.3 |  | 0 | 0
886532 | HPSS 886532 | 155 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1995 | 69 | 28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 69 |  | 0 | 0
903016 | HPSS 903016 | 155 | 4 |  | 1239 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 2006 | 38 | 24.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
942380 | HPSS 942380 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1979 | 55.6 | 36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.6 |  | 0 | 0
942549 | HPSS 942549 | 155 | 3 |  | 1549 | 275 | 183 | UNKV |  | 183 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1982 | 15 | 34.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
942551 | HPSS 942551 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1989 | 31.2 | 31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31.2 |  | 0 | 0
953370 | HPSS 953370 | 155 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1981 | 30.3 | 37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30.3 |  | 0 | 0
993780 | HPSS 993780 | 155 | 4 |  | 1239 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1990 | 35.3 | 32.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35.3 |  | 0 | 0
1051056 | HPSS 1051056 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1965 | 35.7 | 46.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 35.7 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1080568 | HPSS 1080568 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1978 | 51.9 | 36.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51.9 |  | 0 | 0
1100508 | HPSS 1100508 | 155 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1956 | 57.1 | 55.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 57.1 | 0 |  | 0 | 0
1120355 | HPSS 1120355 | 155 | 3 |  | 1549 | 500 | 357 | UNKV |  | 357 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1960 | 88.2 | 51.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 88.2 | 0 |  | 0 | 0
1140264 | HPSS 1140264 | 155 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1989 | 177.9 | 32 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 177.9 |  | 0 | 0
1140310 | HPSS 1140310 | 155 | 3 |  | 1549 | 265 | 176 | UNKV |  | 176 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1960 | 69 | 51.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 69 | 0 |  | 0 | 0
1144094 | HPSS 1144094 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 2005 | 11 | 23 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
1160560 | HPSS 1160560 | 155 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1960 | 76.1 | 51.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 76.1 | 0 |  | 0 | 0
1160598 | HPSS 1160598 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1989 | 67.5 | 31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 67.5 |  | 0 | 0
1160600 | HPSS 1160600 | 155 | 3 |  | 1549 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1972 | 108 | 40.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 108 |  | 0 | 0
1161501 | HPSS 1161501 | 155 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1989 | 44.7 | 31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44.7 |  | 0 | 0
1161513 | HPSS 1161513 | 155 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1990 | 45 | 30.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
1161514 | HPSS 1161514 | 155 | 3 |  | 1549 | 275 | 183 | UNKV |  | 183 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.00% | 3.00% | 1990 | 72.4 | 30.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 72.4 |  | 0 | 0
1161520 | HPSS 1161520 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1990 | 54.8 | 30.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54.8 |  | 0 | 0
1161538 | HPSS 1161538 | 155 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1992 | 58.9 | 29.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58.9 |  | 0 | 0
1161579 | HPSS 1161579 | 155 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1994 | 61 | 28.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 61 |  | 0 | 0
1161587 | HPSS 1161587 | 155 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1995 | 73.2 | 28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 73.2 |  | 0 | 0
1161598 | HPSS 1161598 | 155 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1996 | 55.1 | 27.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
1161642 | HPSS 1161642 | 155 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 2002 | 54 | 24.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
3313800196 | HPSS 3313800196 | 155 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1996 | 415.4 | 28.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 415.4 |  | 0 | 0
3930700600 | HPSS 3930700600 | 155 | 3 |  | 1549 | 350 | 233 | UNKV |  | 233 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 2000 | 82 | 25.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 82 |  | 0 | 0
5339400977 | HPSS 5339400977 | 155 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1992 | 62.2 | 29.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 62.2 |  | 0 | 0
875074 | Service Stub | 155 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.00% | NA | 1996 | 58.7 | 27.5 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58.7 |  | 0 | 0
860102 | HPSS 860102 | 150 | 4 |  | 1239 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1972 | 9.9 | 42.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 9.9 |  | 0 | 0
875124 | HPSS 875124 | 150 | 4 |  | 1239 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1999 | 40 | 28.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
909996 | HPSS 909996 | 150 | 4 |  | 1239 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2000 | 153 | 29.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 153 |  | 0 | 0
991610 | HPSS 991612 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1971 | 102 | 41.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 102 |  | 0 | 0
883055 | HPSS 883055 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1980 | 93 | 36.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 93 |  | 0 | 0
886314 | HPSS 886314 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1992 | 48.1 | 30.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 48.1 |  | 0 | 0
1144044 | HPSS 1144044 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1993 | 63 | 29.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 63 |  | 0 | 0
1160590 | HPSS 1160590 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1979 | 22.1 | 36.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 22.1 |  | 0 | 0
1160610 | HPSS 1160610 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1973 | 56 | 39.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 56 |  | 0 | 0
1161541 | HPSS 1161541 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1992 | 58.1 | 30.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 58.1 |  | 0 | 0
281700921 | HPSS 281700921 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1998 | 81.2 | 27.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 81.2 |  | 0 | 0
1280048 | HPSS 1280048 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1993 | 5.8 | 29.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 5.8 |  | 0 | 0
870372 | HPSS 870372 | 150 | 4 |  | 1239 | 30 | 21 | UNKV |  | 21 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1968 | 10.6 | 46.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 10.6 | 0 |  | 0 | 0
1284940 | HPSS 1284940 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1973 | 75.4 | 39.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 75.4 |  | 0 | 0
1284965 | HPSS 1284965 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1987 | 20.2 | 32.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20.2 |  | 0 | 0
1284975 | HPSS 1284975 | 150 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1984 | 10 | 34.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
1284981 | HPSS 1284981 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1989 | 21.2 | 31.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21.2 |  | 0 | 0
1252340 | HPSS 1252340 | 150 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1969 | 1 | 43.4 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 1 | 0 |  | 0 | 0
860120 | HPSS 860120 | 150 | 4 |  | 1239 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1957 | 83.2 | 66.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 83.2 | 0 |  | 0 | 0
860125 | HPSS 860125 | 150 | 4 |  | 1239 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1963 | 95 | 60.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 95 | 0 |  | 0 | 0
870340 | HPSS 870340 | 150 | 4 |  | 1239 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1960 | 40 | 63.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 40 | 0 |  | 0 | 0
882205 | Service Stub | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1974 | 2 | 48.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
883035 | HPSS 883035 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1963 | 28 | 58.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 28 | 0 |  | 0 | 0
883040 | HPSS 883040 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1962 | 63.9 | 59.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 63.9 | 0 |  | 0 | 0
883050 | HPSS 883050 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1959 | 63.1 | 62.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 63.1 | 0 |  | 0 | 0
883060 | HPSS 883060 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1958 | 82.2 | 63.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 82.2 | 0 |  | 0 | 0
883640 | HPSS 883640 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1971 | 14 | 49.9 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 14 |  | 0 | 0
993600 | HPSS 993600 | 150 | 4 |  | 1239 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1962 | 49 | 61.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 49 | 0 |  | 0 | 0
1140493 | HPSS 1140493 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1963 | 56.4 | 58.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 56.4 | 0 |  | 0 | 0
1140495 | HPSS 1140495 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1962 | 83.7 | 59.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 83.7 | 0 |  | 0 | 0
1252330 | HPSS 1252330 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1960 | 67.5 | 61.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 67.5 | 0 |  | 0 | 0
2930700696 | HPSS 2930700696 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 2000 | 50 | 35.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
3161700755 | HPSS 3161700755 | 150 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1957 | 110 | 65.4 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 110 | 0 |  | 0 | 0
1499083 | HPSS 1499083 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1993 | 58.7 | 29.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 58.7 |  | 0 | 0
1499955 | HPSS 1499955 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2000 | 27.3 | 26.4 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 27.3 |  | 0 | 0
5233800352 | HPSS 5233800352 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1997 | 45.5 | 27.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 45.5 |  | 0 | 0
1281011 | HPSS 1281011 | 150 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1973 | 22 | 39.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
871270 | HPSS 871270 | 150 | 4 |  | 1239 | 225 | 150 | UNKV |  | 150 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1987 | 71 | 33.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 71 |  | 0 | 0
875068 | HPSS 875068 | 150 | 3 |  | 1549 | 225 | 150 | UNKV |  | 150 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1995 | 25 | 27.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
882204 | HPSS 882204 | 150 | 3 |  | 1549 | 225 | 150 | UNKV |  | 150 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.90% | 2.90% | 1967 | 108.3 | 45.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 108.3 | 0 |  | 0 | 0
1160565 | HPSS 1160565 | 150 | 3 |  | 1549 | 225 | 150 | UNKV |  | 150 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1972 | 44 | 39.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
1280050 | HPSS 1280050 | 150 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1993 | 97.1 | 28.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 97.1 |  | 0 | 0
1280497 | HPSS 1280497 | 150 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1997 | 4 | 26.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4 |  | 0 | 0
1284852 | HPSS 1284852 | 150 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1988 | 34.1 | 31.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.1 |  | 0 | 0
1284855 | HPSS 1284855 | 150 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1987 | 19 | 31.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
1284942 | HPSS 1284942 | 150 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1990 | 18.1 | 30.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18.1 |  | 0 | 0
1284978 | HPSS 1284978 | 150 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1985 | 15 | 32.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
1495050 | HPSS 1495050 | 150 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1988 | 7 | 31.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
1499327 | HPSS 1499327 | 150 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1995 | 20 | 27.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
346015008 | HPSS 346015008 | 150 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2016 | 64 | 17.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 64 |  | 0 | 0
1160180386 | HPSS 1160180386 | 150 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 2011 | 62 | 19.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 62 |  | 0 | 0
6658900642 | HPSS 6658900642 | 150 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.90% | NA | 1995 | 50.6 | 27.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50.6 |  | 0 | 0
20943 | Inlet 005-R-001 | 155 | 3 |  | 1662 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.188 | 35000 | 0.6 | NO | NA | NA | 2.80% | NA | 1972 | 25 | 45.3 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
A0070908 | Inlet 005-R-142 | 150 | 3 |  | 1106 | 375 | 250 | 275 |  | 250 | X | X | VALID | 2.375 | 0.218 | 35000 | 0.6 | NO | NO | YES | 2.33% | 4.07% | 2004 | 28 | 20.57 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 28 | 1 | 0 | 28 |  | 1
235969 | Bellingham H.P. Distribution System | 150 | 3 |  | 2269 | 700 | 466 | 250 |  | 250 | X | X | VALID | 2.375 | 0.154 | 52000 | 1 | NO | NO | NO | 2.22% | 3.30% | 2017 | 375 | 12.3 | No Action Needed | -- | 1 | 1 | 0 | 375 | 1 | 0 | 375 |  | 1
886804 | HPSS 886804 | 155 | 3 |  | 2260 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 2.06% | NA | 2000 | 32 | 20.56 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 32 |  | 0 | 0
947446 | HPSS 947446 | 155 | 3 |  | 2260 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 2.06% | NA | 2000 | 19 | 20.56 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
A0072325 | Main to HPSS 1140310 & 1144089 | 155 | 3 |  | 1549 | 265 | 176 | 1200 |  | 176 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | YES | YES | 2.06% | 3.00% | 2004 | 51.8 | 23.5 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 51.8 |  | 0 | 0
A0081220 | Inlet 005-R-157 | 150 | 3 |  | 1193 | 90 | 60 | 1440 |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | YES | YES | 1.99% | 3.77% | 2006 | 29.2 | 24.27 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 29.2 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
BremertonL2-1 | 8" & 12" Bremerton Transmission Line | 499 | 3 |  | 704 | 750 | 535 | NA |  | 535 | X | NA | VALID | 8.625 | 0.188 | 40400 | 0.8 | NO | NO | YES | 28.33% | 19.09% | 1963 | 2851.2 | 116.33 | Accept Most Stringent Criteria | -- | 1 | 0 | 2851.2 | 0 | 1 | 2851.2 | 0 | 1
20C6308-B | 8" Kitsap Line | 499 | 3 |  | 802 | 750 | 535 | 720 |  | 535 | X | NA | VALID | 8.625 | 0.188 | 46000 | 0.8 | NO | YES | YES | 24.88% | 24.88% | 1964 | 82958.2 | 113.38 | Accept Most Stringent Criteria | -- | 1 | 0 | 82958.2 | 0 | 1 | 82958.2 | 0 | 1
20C6308-B | 8" Kitsap Line | 499 | 3 |  | 758 | 750 | 535 | 720 |  | 535 | X | NA | VALID | 4.5 | 0.237 | 24000 | 0.6 | NO | NO | YES | 19.74% | 19.09% | 1964 | 4.3 | 75.74 | Accept Most Stringent Criteria | -- | 1 | 0 | 4.3 | 0 | 1 | 4.3 | 0 | 1
50203 | 8" Kitsap Line (008-V-156) | 499 | 3 |  | 418 | 750 | 500 | 720 |  | 418 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 47.69% | NA | 1996 | 0 | 112.19 | In-Situ Test | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
51772 | Inlet 008-R-017 | 499 | 3 |  | 1045 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.322 | 46000 | 0.8 | NO | YES | YES | 14.53% | 19.09% | 1963 | 74.2 | 106.09 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 74.2 | 0 |  | 0 | 0
UNKV (R-9) | Inlet 008-R-009 | 499 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 29.99% | 29.99% | 1994 | 16.3 | 105.49 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 16.3 |  | 0 | 0
53353 | 8" & 12" Bremerton Transmission Line | 499 | 3 |  | 823 | 1200 | 800 | 720 |  | 720 | X | NA | VALID | 12.75 | 0.312 | 52000 | 0.8 | NO | YES | YES | 19.61% | 24.24% | 1964 | 1959.6 | 105.24 | Accept Most Stringent Criteria | -- | 1 | 0 | 1959.6 | 0 | 1 | 1959.6 | 0 | 1
20C6316 (144) | 8" Bremerton H.P. Line | 144 | 4 |  | 334 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 46000 | 0.8 | YES | YES | YES | 7.18% | 13.76% | 1964 | 5836.7 | 101.76 | 116 Segment, Replace | 2020 | 1 | 0 | 5836.7 | 0 |  | 0 | 0
13740 | Main Stub | 499 | 3 |  | 1193 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 12.54% | NA | 1968 | 0.7 | 84.54 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 0.7 | 0 |  | 0 | 0
17542 | Main Stub | 144 | 3 |  | 1361 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NA | NA | 3.17% | NA | 1970 | 2 | 38.67 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 2 | 0 |  | 0 | 0
22C6310 | 4" Port Orchard H.P. Line | 170 | 3 |  | 499 | 350 | 233 | NA |  | 233 | X | NA | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 10.22% | 10.22% | 1963 | 20757.2 | 82.22 | Accept Most Stringent Criteria | -- | 1 | 0 | 20757.2 | 0 | 1 | 20757.2 | 0 | 1
25293 | Inlet 008-R-064 | 250 | 3 |  | 499 | 0 | 0 | 400 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1977 | 9 | 79.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 9 |  | 0 | 0
202359 | 8" Kitsap Line | 499 | 3 |  | 933 | 796 | 530 | 720 |  | 530 | X | NA | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | YES | YES | 16.55% | 16.03% | 1964 | 664.9 | 77.55 | Accept Most Stringent Criteria | -- | 1 | 0 | 664.9 | 0 | 1 | 664.9 | 0 | 1
20C6316 (250) | 8” West Bremerton H.P. Line | 250 | 3 |  | 802 | 350 | 233 | NA |  | 233 |  | NA | UNVALID | 8.625 | 0.188 | 46000 | 0.8 | NO | NA | NA | 12.47% | NA | 1964 | 4175.8 | 76.97 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 4175.8 | 0 |  | 0 | 0
25745 | 8" North Kitsap H.P. Line | 250 | 3 |  | 544 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 8.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 16.38% | 18.35% | 1978 | 12186.1 | 76.85 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12186.1 |  | 0 | 0
25288 | 8" North Kitsap H.P. Line | 250 | 3 |  | 610 | 600 | 400 | 400 |  | 400 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 16.38% | 9.57% | 1977 | 37579.6 | 76.38 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 37579.6 | 1 | 0 | 37579.6 |  | 1
16135 | 2" Belfair H.P. Line | 499 | 3 |  | 933 | 960 | 685 | 1440 |  | 685 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 10.99% | 16.03% | 1970 | 5230.2 | 76.03 | Accept Most Stringent Criteria | -- | 1 | 0 | 5230.2 | 0 | 1 | 5230.2 | 0 | 1
10362 | Inlet 008-R-021 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 8.03% | 1966 | 21 | 75.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 21 | 0 |  | 0 | 0
50201 | 12" Kitsap H.P. Line | 499 | 3 |  | 1017 | 1080 | 720 | 720 |  | 720 | X | X | VALID | 12.75 | 0.312 | 52000 | 0.8 | NO | NO | YES | 19.61% | 19.61% | 1996 | 71564.6 | 75.11 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 71564.6 | 1 | 0 | 71564.6 |  | 1
20387 | 4" Olympic View H.P. Line | 499 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 17.06% | 13.54% | 1973 | 14110.1 | 74.06 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 14110.1 | 1 | 0 | 14110.1 |  | 1
22C9362 | Main Stub | 170 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 5.46% | 5.46% | 1965 | 3 | 73.96 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 3 | 0 |  | 0 | 0
16443 | Inlet 008-R-019 | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1969 | 10 | 72.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 10 | 0 |  | 0 | 0
UNKV (22C6310) | 4” Port Orchard H.P. Line (008-R-013) | 170 | 3 |  | 877 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 5.81% | NA | 1963 | 28 | 72.31 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 28 | 0 |  | 0 | 0
13349 | Inlet 008-R-008, 008-R-009, | 499 | 3 |  | 499 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 12.54% | 10.22% | 1967 | 12.5 | 70.54 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 12.5 | 0 |  | 0 | 0
45000 | 6" Bangor H.P. Line | 250 | 3 |  | 544 | 600 | 400 | 275 |  | 275 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 18.35% | 1993 | 10080.7 | 69.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 10080.7 | 1 | 0 | 10080.7 |  | 1
51773 | 008-R-022 | 144 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 9.44% | 13.76% | 1996 | 121.3 | 69.26 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 121.3 |  | 0 | 0
18522 | 8" Bremerton H.P. Line | 144 | 3 |  | 418 | 350 | 250 | UNKV |  | 250 | X |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 13.76% | 13.76% | 1971 | 2799.8 | 68.26 | 116 Segment, Replace | 2020 | 1 | 1 | 0 | 2799.8 |  | 0 | 0
1700754 | HPSS 1700754 | 499 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 9.66% | 9.66% | 1970 | 93.1 | 68.16 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 93.1 | 0 |  | 0 | 0
23424 | Inlet 008-R-024 | 250 | 3 |  | 499 | 114 | 76 | NA |  | 76 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1974 | 29.5 | 65.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 29.5 |  | 0 | 0
29628 | Inlet 008-R-051 | 250 | 3 |  | 499 | 600 | 1 | UNKV |  | 1 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 8.55% | 15.02% | 1982 | 479.6 | 62.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 479.6 |  | 0 | 0
175846 | Inlet 008-R-136 | 499 | 3 |  | 1549 | 100 | 66 | 720 |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 9.66% | 9.66% | 1967 | 18 | 61.16 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 18 | 0 |  | 0 | 0
1950810 | HPSS 1950810 | 499 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1967 | 38 | 61.16 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 38 | 0 |  | 0 | 0
25292 | Inlet 008-R-053 | 250 | 3 |  | 1361 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1977 | 46.1 | 60.51 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 46.1 |  | 0 | 0
1700750 | HPSS 1700750 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1963 | 50 | 60.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 50 | 0 |  | 0 | 0
218405 | Main to HPSS 1578402, 1578407, 1578408 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1989 | 155.1 | 60.28 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 155.1 |  | 0 | 0
28123 | 8" North Kitsap H.P. Line | 250 | 3 |  | 849 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 8.625 | 0.203 | 46000 | 0.8 | NO | NO | YES | 11.78% | 9.57% | 1980 | 9708.9 | 60.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 9708.9 | 1 | 0 | 9708.9 |  | 1
1703536 | HPSS 1703536 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 9.66% | 9.66% | 1963 | 27.1 | 60.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 27.1 | 0 |  | 0 | 0
1700293 | Service Stub | 144 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 4.63% | 1963 | 33 | 60.13 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 33 | 0 |  | 0 | 0
22C6318 | 4" Port Orchard H.P. Line | 170 | 3 |  | 877 | 350 | 233 | NA |  | 233 | X | NA | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 5.81% | NA | 1963 | 3525.3 | 59.81 | Accept Most Stringent Criteria | -- | 1 | 0 | 3525.3 | 0 | 1 | 3525.3 | 0 | 1
32585 | Main Stub | 250 | 3 |  | 877 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1985 | 2 | 59.55 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 2 |  | 0 | 0
20C7461 | Main Stub | 144 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 4.63% | NA | 1964 | 19.9 | 59.13 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 19.9 | 0 |  | 0 | 0
1680355 | Service Stub | 144 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1963 | 9 | 58.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 9 | 0 |  | 0 | 0
B0073116 | 6" North Bremerton H.P. Line | 250 | 3 |  | 660 | 740 | 493 | 720 |  | 493 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 12.59% | 8.45% | 2004 | 14173.5 | 58.09 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 14173.5 | 1 | 0 | 14173.5 |  | 1
29413 | 6" Bangor H.P. Line | 250 | 3 |  | 802 | 600 | 400 | NA |  | 400 | X | X | VALID | 8.625 | 0.188 | 46000 | 0.8 | NO | NO | YES | 12.47% | 9.57% | 1981 | 1165.1 | 57.97 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1165.1 | 1 | 0 | 1165.1 |  | 1
2416 | Inlet 008-R-064 | 250 | 3 |  | 877 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 8.55% | NA | 1992 | 3 | 56.05 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 3 |  | 0 | 0
57079 | Inlet 008-R-149 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | YES | YES | 5.51% | 8.03% | 1999 | 87 | 56.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 87 |  | 0 | 0
16599 | Main Stub | 170 | 3 |  | 933 | 100 | 66 | 250 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.75% | 5.46% | 1969 | 3 | 54.96 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 3 | 0 |  | 0 | 0
47760 | 8" Bremerton H.P. Line | 144 | 4 |  | 435 | 850 | 566 | UNKV |  | 435 | X | X | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 7.25% | 10.57% | 1996 | 1171.5 | 54.57 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1171.5 |  | 0 | 0
25289 | 6" North Bremerton H.P. Line | 250 | 3 |  | 794 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NA | NA | 12.59% | NA | 1977 | 129.5 | 53.59 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 129.5 |  | 0 | 0
49319 | 6" Port Orchard H.P. Loop Line | 170 | 3 |  | 794 | 600 | 400 | 720 |  | 400 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 8.56% | 5.75% | 1995 | 11246.1 | 53.56 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 11246.1 | 1 | 0 | 11246.1 |  | 1
B0071949 | M&R B0071949 | 499 | 3 |  | 908 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 18.89% | 21.96% | 2004 | 42.5 | 53.46 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 42.5 | 1 | 0 | 42.5 |  | 1
33043 | 8" Bremerton H.P. Line | 144 | 3 |  | 418 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 13.76% | 4.63% | 1986 | 44.7 | 53.26 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 44.7 |  | 0 | 0
1670366 | Service Stub | 144 | 4 |  | 746 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 4.63% | 1963 | 10.1 | 53.13 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 10.1 | 0 |  | 0 | 0
41121 | Inlet 008-R-006 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 10.99% | 10.99% | 1974 | 44.1 | 52.49 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 44.1 | 1 | 0 | 44.1 |  | 1
1703537 | HPSS 1703537 | 499 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1980 | 38 | 52.16 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 38 |  | 0 | 0
1670370 | Service Stub | 144 | 4 |  | 746 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 4.63% | 1964 | 10 | 52.13 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 10 | 0 |  | 0 | 0
26761 | Inlet 008-R-049 | 250 | 3 |  | 933 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | YES | YES | 5.51% | 8.03% | 1979 | 226.4 | 52.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 226.4 |  | 0 | 0
1950838 | HPSS 1950838 | 499 | 3 |  | 1549 | 325 | 216 | UNKV |  | 216 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1981 | 3 | 51.66 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 3 |  | 0 | 0
2000414 | Service Stub | 250 | 3 |  | 933 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 8.03% | 1978 | 19 | 51.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 19 |  | 0 | 0
41069 | Inlet 008-R-064 | 250 | 3 |  | 499 | 600 | 400 | UNKV |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 8.55% | 15.02% | 1992 | 16.2 | 51.52 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.2 |  | 0 | 0
1670340 | HPSS 1670340 | 144 | 4 |  | 1239 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1963 | 6 | 51.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 6 | 0 |  | 0 | 0
1670360 | HPSS 1670360 | 144 | 4 |  | 1239 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1963 | 26.1 | 51.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 26.1 | 0 |  | 0 | 0
2045130 | HPSS 2045130 | 250 | 3 |  | 1193 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1977 | 130.8 | 51.28 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 130.8 |  | 0 | 0
1670391 | Service Stub | 144 | 4 |  | 746 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 4.63% | 1965 | 5 | 51.13 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 5 | 0 |  | 0 | 0
16442 | Inlet 008-R-019 | 250 | 3 |  | 1361 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1969 | 38.8 | 51.01 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 38.8 | 0 |  | 0 | 0
2045121 | HPSS 2045121 | 250 | 3 |  | 1193 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 6.28% | NA | 1978 | 236.2 | 50.78 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 236.2 |  | 0 | 0
2045249 | HPSS 2045249 | 250 | 3 |  | 1193 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1978 | 153.1 | 50.78 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 153.1 |  | 0 | 0
1700745 | HPSS 1700745 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1964 | 50 | 50.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 50 | 0 |  | 0 | 0
1510080 | HPSS 1510080 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1963 | 59.1 | 49.79 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 59.1 | 0 |  | 0 | 0
2045128 | HPSS 2045128 | 250 | 3 |  | 1193 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1978 | 51 | 49.78 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 51 |  | 0 | 0
2045140 | HPSS 2045140 | 250 | 3 |  | 1193 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1978 | 85.1 | 49.78 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 85.1 |  | 0 | 0
57229 | 8" Bremerton H.P. Line | 144 | 4 |  | 334 | 748 | 498 | NA |  | 334 | X |  | UNVALID | 8.625 | 0.322 | 35000 | 0.8 | NO | YES | YES | 5.51% | 13.76% | 1999 | 185.1 | 49.76 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 185.1 |  | 0 | 0
41124 | Inlet 008-R-028 | 499 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 17.06% | 13.54% | 1992 | 20.1 | 49.56 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 20.1 |  | 0 | 0
2000417 | HPSS 2000417 | 250 | 3 |  | 933 | 125 | 83 | NA |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 8.03% | 1984 | 108.1 | 49.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 108.1 |  | 0 | 0
1700741 | HPSS 1700741 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1965 | 19 | 49.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 19 | 0 |  | 0 | 0
1671119 | HPSS 1671119 | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1963 | 15 | 49.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 15 | 0 |  | 0 | 0
1671082 | Service Stub | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1963 | 61 | 49.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 61 | 0 |  | 0 | 0
1796950 | HPSS 1796950 | 499 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1988 | 127.7 | 49.16 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 127.7 |  | 0 | 0
32756 | Inlet 008-R-070 | 250 | 3 |  | 933 | 125 | 83 | 1440 |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1985 | 161 | 49.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 161 |  | 0 | 0
2001648 | HPSS 2001648 | 250 | 3 |  | 933 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 8.03% | 1985 | 290.3 | 49.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 290.3 |  | 0 | 0
40402 | 8" North Kitsap H.P. Line | 250 | 3 |  | 610 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 16.38% | 9.57% | 1992 | 20.2 | 48.88 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20.2 | 1 | 0 | 20.2 |  | 1
1510070 | Inlet 008-R-146 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1964 | 54.1 | 48.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 54.1 | 0 |  | 0 | 0
2045255 | HPSS 2045255 | 250 | 3 |  | 1193 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1982 | 209.2 | 48.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 209.2 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
31859 | Inlet 008-R-066 | 250 | 3 |  | 933 | 600 | 400 | 250 |  | 250 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1984 | 516.9 | 48.53 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 516.9 | 1 | 0 | 516.9 |  | 1
1700760 | HPSS 1700760 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1966 | 15 | 48.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 15 | 0 |  | 0 | 0
1700740 | HPSS 1700740 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1965 | 14 | 48.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 14 | 0 |  | 0 | 0
31584 | Inlet 008-R-048 | 250 | 3 |  | 933 | 105 | 70 | 1440 |  | 70 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1985 | 25 | 48.03 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
33071 | Inlet 008-R-065 | 250 | 3 |  | 933 | 125 | 83 | 1440 |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1985 | 20 | 48.03 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1510040 | HPSS 1510040 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1965 | 66.8 | 47.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 66.8 | 0 |  | 0 | 0
1510050 | HPSS 1510050 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1965 | 9 | 47.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 9 | 0 |  | 0 | 0
2045207 | HPSS 2045207 | 250 | 3 |  | 1193 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1984 | 171 | 47.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 171 |  | 0 | 0
B0080216 | Inlet 008-R-124 | 170 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 5.46% | 5.46% | 2011 | 7.4 | 47.46 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 7.4 |  | 0 | 0
1671124 | HPSS 1671124 | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1965 | 12 | 47.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 12 | 0 |  | 0 | 0
59179 | 8" Bremerton H.P. Line | 144 | 3 |  | 418 | 750 | 500 | UNKV |  | 418 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | YES | YES | YES | 7.10% | 13.76% | 2000 | 148.1 | 47.26 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 148.1 |  | 0 | 0
1510073 | HPSS 1510073 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1966 | 18 | 46.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 18 | 0 |  | 0 | 0
2043932 | HPSS 2043932 | 250 | 3 |  | 1193 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1984 | 97.1 | 46.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 97.1 |  | 0 | 0
2045261 | HPSS 2045261 | 250 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1984 | 97.1 | 46.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 97.1 |  | 0 | 0
1796000 | HPSS 1796000 | 499 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1991 | 32 | 46.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 32 |  | 0 | 0
1796001 | HPSS 1796001 | 499 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1991 | 59 | 46.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 59 |  | 0 | 0
53133 | 6" Port Orchard H.P. Loop Line (008-V-168) | 170 | 3 |  | 544 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.81% | 12.48% | 1997 | 44 | 46.48 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 44 |  | 0 | 0
B0084415 | 8" North Kitsap H.P. Line | 250 | 3 |  | 556 | 710 | 473 | UNKV |  | 473 | X |  | UNVALID | 8.625 | 0.25 | 24000 | 0.8 | YES | NA | NA | 17.97% | NA | 2008 | 43 | 46.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
2045197 | HPSS 2045197 | 250 | 3 |  | 1193 | 125 | 83 | NA |  | 83 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 6.28% | NA | 1985 | 82.1 | 46.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 82.1 |  | 0 | 0
1795130 | HPSS 1795130 | 499 | 3 |  | 1549 | 600 | 400 | NA |  | 400 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 9.66% | NA | 1992 | 59 | 46.16 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 59 |  | 0 | 0
184804 | Inlet 008-R-145 | 250 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1979 | 49.4 | 46.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.4 |  | 0 | 0
25294 (R-62) | Inlet 008-R-062 | 250 | 3 |  | 1361 | 115 | 76 | 1440 |  | 76 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1978 | 235.2 | 46.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 235.2 |  | 0 | 0
25294 (R-63) | Inlet 008-R-063 | 250 | 3 |  | 1361 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NA | NA | 5.51% | NA | 1978 | 140.1 | 46.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 140.1 |  | 0 | 0
1510076 | HPSS 1510076 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1967 | 45 | 45.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 45 | 0 |  | 0 | 0
1950210 | HPSS 1950210 | 170 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1967 | 61.7 | 45.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 61.7 | 0 |  | 0 | 0
2045251 | HPSS 2045251 | 250 | 3 |  | 1193 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 6.28% | NA | 1986 | 69.1 | 45.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 69.1 |  | 0 | 0
B0065951 | 8" Bremerton H.P. Line | 144 | 3 |  | 418 | 705 | 470 | NA |  | 418 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 9.44% | 13.76% | 2001 | 41.5 | 45.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 41.5 | 1 | 0 | 41.5 |  | 1
44274 | 6" Port Orchard H.P. Loop Line | 170 | 3 |  | 794 | 750 | 500 | NA |  | 500 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 8.56% | 5.75% | 1993 | 9307 | 45.56 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 9307 | 1 | 0 | 9307 |  | 1
2001103 | HPSS 2001103 | 250 | 3 |  | 933 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 8.03% | 1992 | 116.1 | 45.53 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 116.1 |  | 0 | 0
2043902 | HPSS 2043902 | 250 | 3 |  | 1193 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1987 | 43 | 45.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
16988 | Inlet 008-R-025 | 144 | 3 |  | 933 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | YES | YES | 3.17% | 4.63% | 1969 | 13.1 | 45.13 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 13.1 | 0 |  | 0 | 0
41077 | Inlet 008-R-068 | 250 | 3 |  | 794 | 600 | 400 | 720 |  | 400 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 12.59% | 8.45% | 1992 | 30.2 | 45.09 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 30.2 | 1 | 0 | 30.2 |  | 1
1625 | M&R 47761 | 144 | 3 |  | 544 | 850 | 566 | NA |  | 544 | X | Service | VALID | 6.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 10.57% | NA | 1996 | 2 | 45.07 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2 | 1 | 0 | 2 |  | 1
45222 | Port Orchard Check Meter M&R 45222 | 499 | 3 |  | 1106 | 750 | 500 | NA |  | 500 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 13.54% | 13.54% | 1994 | 21.9 | 45.04 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21.9 | 1 | 0 | 21.9 |  | 1
25654 | Inlet 008-R-045 | 250 | 3 |  | 1361 | 108 | 72 | 1440 |  | 72 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1978 | 67.1 | 45.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 67.1 |  | 0 | 0
25876 | Inlet 008-R-050 | 250 | 3 |  | 1361 | 115 | 76 | 1440 |  | 76 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1978 | 65.1 | 45.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 65.1 |  | 0 | 0
25899 | Inlet 008-R-067 | 250 | 3 |  | 1361 | 105 | 70 | 1440 |  | 70 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1978 | 46.4 | 45.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 46.4 |  | 0 | 0
1950256 | HPSS 1950256 | 170 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1968 | 18 | 44.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 18 | 0 |  | 0 | 0
1951000 | HPSS 1951000 | 170 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1968 | 82.1 | 44.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 82.1 | 0 |  | 0 | 0
1510078 | Service Stub | 170 | 3 |  | 1549 | 90 | 64 | UNKV |  | 64 |  |  | UNVALID | NA | NA | NA | NA | YES | YES | YES | NA | 3.29% | 1968 | 39 | 44.79 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 39 | 0 |  | 0 | 0
B0085444 | 8" Bremerton H.P. Line | 144 | 4 |  | 334 | 440 | 293 | UNKV |  | 293 | X |  | UNVALID | 8.625 | 0.25 | 52000 | 0.8 | YES | YES | YES | 4.78% | 13.76% | 2009 | 174.2 | 44.76 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 174.2 |  | 0 | 0
1670362 | Service Stub | 144 | 4 |  | 746 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 4.63% | 1971 | 9.1 | 44.63 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 9.1 |  | 0 | 0
25871 | Inlet 008-R-081 | 250 | 3 |  | 1361 | 120 | 80 | 1440 |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1979 | 85.1 | 44.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 85.1 |  | 0 | 0
26706 | Main Stub | 250 | 3 |  | 1361 | 120 | 80 | 1440 |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1979 | 6 | 44.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
1700784 | HPSS 1700784 | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1968 | 45 | 44.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 45 | 0 |  | 0 | 0
1702974 | HPSS 1702974 | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1968 | 14 | 44.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 14 | 0 |  | 0 | 0
1702979 | HPSS 1702979 | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1968 | 41 | 44.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 41 | 0 |  | 0 | 0
1702980 | HPSS 1702980 | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1968 | 42 | 44.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 42 | 0 |  | 0 | 0
1578407 | HPSS 1578407 | 250 | 3 |  | 1193 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 6.28% | 1991 | 152 | 44.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 152 |  | 0 | 0
218194 | Inlet 008-R-153 | 250 | 3 |  | 1193 | 745 | 496 | UNKV |  | 496 | X | X | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 6.28% | 6.28% | 1979 | 79.3 | 44.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 79.3 |  | 0 | 0
41118 | Outlet 008-R-028 | 250 | 3 |  | 794 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 12.59% | 9.57% | 1994 | 17.6 | 44.09 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 17.6 |  | 0 | 0
28251 | Inlet 008-R-055 | 250 | 3 |  | 1361 | 120 | 80 | 1440 |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1980 | 17.1 | 44.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 17.1 |  | 0 | 0
40417 | Inlet 008-R-040 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 10.99% | 10.99% | 1991 | 25 | 43.99 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 25 |  | 0 | 0
2001016 | HPSS 2001016 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 343.3 | 43.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 343.3 |  | 0 | 0
28962 | Inlet 008-R-058 | 250 | 3 |  | 1361 | 120 | 80 | 1440 |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1981 | 1.1 | 43.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 1.1 |  | 0 | 0
53149 | 8" North Kitsap H.P. Line | 250 | 3 |  | 811 | 700 | 466 | 720 |  | 466 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 12.32% | 9.57% | 1997 | 421.8 | 43.32 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 421.8 | 1 | 0 | 421.8 |  | 1
1671115 | HPSS 1671115 | 144 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1969 | 26 | 43.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 26 | 0 |  | 0 | 0
1700307 | Inlet 008-R-129 | 144 | 3 |  | 1549 | 100 | 71 | 1440 |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.79% | NA | 1969 | 72.1 | 43.29 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 72.1 | 0 |  | 0 | 0
2044853 | HPSS 2044853 | 250 | 3 |  | 1193 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1991 | 80.1 | 43.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 80.1 |  | 0 | 0
1950991 | HPSS 1950991 | 499 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 9.66% | NA | 1998 | 7 | 43.16 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
1950993 | HPSS 1950993 | 499 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 9.66% | 9.66% | 1998 | 3.1 | 43.16 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 3.1 |  | 0 | 0
1670386 | Service Stub | 144 | 4 |  | 746 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 4.63% | 1974 | 5 | 43.13 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 5 |  | 0 | 0
1510047 | HPSS 1510047 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1969 | 14 | 42.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 14 | 0 |  | 0 | 0
24684 | Inlet 008-R-027 | 499 | 3 |  | 2123 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 7.05% | NA | 1976 | 59.1 | 42.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 59.1 | 1 | 0 | 59.1 |  | 1
B0078444 | Inlet 008-R-127 | 499 | 3 |  | 1193 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 10.99% | 12.54% | 2005 | 20.4 | 42.54 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20.4 | 1 | 0 | 20.4 |  | 1
169896 | 4" Olympic View H.P. Line | 499 | 3 |  | 1106 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 52000 | 0.6 | NO | NO | YES | 11.48% | 13.54% | 2009 | 583.5 | 42.54 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 583.5 |  | 0 | 0
1700670 | Service Stub | 144 | 3 |  | 933 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 4.63% | 1972 | 39.1 | 42.13 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 39.1 |  | 0 | 0
31494 | Inlet 008-R-059 | 250 | 3 |  | 1361 | 125 | 83 | 1440 |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1984 | 16.1 | 42.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 16.1 |  | 0 | 0
31570 | Inlet 008-R-052 | 250 | 3 |  | 1361 | 120 | 80 | 1440 |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1984 | 49.1 | 42.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 49.1 |  | 0 | 0
31583 | Inlet 008-R-057 | 250 | 3 |  | 1361 | 125 | 83 | 1440 |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1984 | 14 | 42.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
1510079 | HPSS 1510079 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1970 | 34 | 41.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 34 | 0 |  | 0 | 0
2043860 | HPSS 2043860 | 250 | 3 |  | 1193 | 780 | 520 | UNKV |  | 520 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1984 | 47.5 | 41.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47.5 |  | 0 | 0
1796955 | HPSS 1796955 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1991 | 57.4 | 41.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.4 |  | 0 | 0
32190 | Inlet 008-R-056 | 250 | 3 |  | 1361 | 125 | 83 | 1440 |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1985 | 38.3 | 41.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 38.3 |  | 0 | 0
32382 | Inlet 008-R-071 | 250 | 3 |  | 1361 | 125 | 83 | 250 |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1985 | 20 | 41.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
32852 | Inlet 008-R-080 | 250 | 3 |  | 1361 | 125 | 83 | 1440 |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1985 | 32.8 | 41.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 32.8 |  | 0 | 0
1950235 | HPSS 1950235 | 170 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1971 | 25.9 | 41.29 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25.9 |  | 0 | 0
1950950 | HPSS 1950950 | 170 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1971 | 75.1 | 41.29 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 75.1 |  | 0 | 0
53128 | 6" Port Orchard H.P. Loop Line | 170 | 3 |  | 1044 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.188 | 46000 | 0.8 | NO | NO | YES | 6.51% | 5.75% | 1998 | 9495.5 | 41.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 9495.5 | 1 | 0 | 9495.5 |  | 1
46426 | Inlet 008-R-102 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 10.99% | 10.99% | 1997 | 34.1 | 40.99 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 34.1 | 1 | 0 | 34.1 |  | 1
2001085 | HPSS 2001085 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1977 | 160.2 | 40.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 160.2 |  | 0 | 0
2001777 | HPSS 2001777 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1977 | 137.1 | 40.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 137.1 |  | 0 | 0
1700426 | HPSS 1700426 | 144 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1971 | 4.1 | 40.79 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 4.1 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
2045206 | HPSS 2045206 | 250 | 3 |  | 1193 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 6.28% | NA | 1996 | 30 | 40.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
2000125 | HPSS 2000125 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 206.2 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 206.2 |  | 0 | 0
2000130 | HPSS 2000130 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 148.1 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 148.1 |  | 0 | 0
2001095 | HPSS 2001095 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 150.1 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 150.1 |  | 0 | 0
2001363 | HPSS 2001363 | 250 | 3 |  | 1549 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 122.1 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 122.1 |  | 0 | 0
2001440 | HPSS 2001440 | 250 | 3 |  | 1549 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 120.1 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 120.1 |  | 0 | 0
2001520 | HPSS 2001520 | 250 | 3 |  | 1549 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 134.1 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 134.1 |  | 0 | 0
25874 | Inlet 008-R-032 | 170 | 3 |  | 877 | 375 | 250 | 720 |  | 250 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.81% | 4.61% | 1978 | 47.4 | 40.31 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 47.4 | 1 | 0 | 47.4 |  | 1
1951006 | Service Stub | 170 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1973 | 52.4 | 40.29 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 52.4 |  | 0 | 0
1510095 | HPSS 1510095 | 170 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1991 | 33 | 40.29 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 33 |  | 0 | 0
2045188 | HPSS 2045188 | 250 | 3 |  | 1193 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 6.28% | NA | 1997 | 18 | 40.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
1796957 | HPSS 1796957 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1996 | 226.8 | 40.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 226.8 |  | 0 | 0
1950815 | HPSS 1950815 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1994 | 16 | 40.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
1950829 | HPSS 1950829 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1996 | 132.1 | 40.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 132.1 |  | 0 | 0
40558 | Inlet 008-R-042 | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.28% | 1992 | 37 | 40.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 37 | 1 | 0 | 37 |  | 1
34818 | Inlet 008-R-148 | 250 | 3 |  | 1361 | 90 | 60 | 1440 |  | 60 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1988 | 78 | 40.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 78 |  | 0 | 0
35662 | Inlet 008-R-061 | 250 | 3 |  | 1361 | 90 | 60 | 1440 |  | 60 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1988 | 71.1 | 40.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 71.1 |  | 0 | 0
41106 | Inlet 008-R-082 | 250 | 3 |  | 1361 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1978 | 13.7 | 40.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 13.7 |  | 0 | 0
2000112 | HPSS 2000112 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1977 | 62.1 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 62.1 |  | 0 | 0
2000127 | HPSS 2000127 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1979 | 194.2 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 194.2 |  | 0 | 0
2000405 | HPSS 2000405 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1977 | 78.1 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 78.1 |  | 0 | 0
2000427 | HPSS 2000427 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1977 | 80 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 80 |  | 0 | 0
2000445 | HPSS 2000445 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1977 | 66.1 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 66.1 |  | 0 | 0
2000458 | HPSS 2000458 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 105.1 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 105.1 |  | 0 | 0
2000459 | HPSS 2000459 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 183.2 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 183.2 |  | 0 | 0
2001064 | HPSS 2001064 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 171.2 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 171.2 |  | 0 | 0
2001355 | HPSS 2001355 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1979 | 278.4 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 278.4 |  | 0 | 0
2001485 | HPSS 2001485 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 131.1 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 131.1 |  | 0 | 0
2001662 | HPSS 2001662 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1977 | 72.1 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 72.1 |  | 0 | 0
2001779 | HPSS 2001779 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 123.1 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 123.1 |  | 0 | 0
2000442 | HPSS 2000442 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1975 | 13 | 39.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
1510038 | HPSS 1510038 | 170 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1974 | 66 | 39.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 66 |  | 0 | 0
1950259 | HPSS 1950259 | 170 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1974 | 61 | 39.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 61 |  | 0 | 0
222042 | 8" Bremerton H.P. Line | 144 | 3 |  | 418 | 268 | 178 | NA |  | 178 | X | X | VALID | 8.625 | 0.322 | 52000 | 0.8 | NO | YES | YES | 3.71% | 13.76% | 2015 | 238.5 | 39.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 238.5 | 1 | 0 | 238.5 |  | 1
1950952 | HPSS 1950952 | 499 | 3 |  | 1549 | 750 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2005 | 9 | 39.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
1796003 | HPSS 1796003 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1995 | 18 | 39.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
1796004 | HPSS 1796004 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1995 | 42 | 39.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
2001074 | HPSS 2001074 | 250 | 3 |  | 933 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 8.03% | 1992 | 40 | 39.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
2000128 | HPSS 2000128 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 97.1 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 97.1 |  | 0 | 0
2000147 | HPSS 2000147 | 250 | 3 |  | 1549 | 105 | 70 | UNKV |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 80.1 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 80.1 |  | 0 | 0
2001060 | HPSS 2001060 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 40 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
2001079 | HPSS 2001079 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 55.9 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 55.9 |  | 0 | 0
2001385 | HPSS 2001385 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 86 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 86 |  | 0 | 0
2001454 | HPSS 2001454 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 55.1 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
2001455 | HPSS 2001455 | 250 | 3 |  | 1549 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 57.1 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 57.1 |  | 0 | 0
2001522 | HPSS 2001522 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 176.2 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 176.2 |  | 0 | 0
2001524 | HPSS 2001524 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 255.3 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 255.3 |  | 0 | 0
2043460 | HPSS 2043460 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 54 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
2043645 | HPSS 2043645 | 250 | 3 |  | 1549 | 105 | 70 | NA |  | 70 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1978 | 48.9 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 48.9 |  | 0 | 0
2000188 | HPSS 2000188 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 45 | 39.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
2001548 | HPSS 2001548 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1976 | 48.1 | 39.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48.1 |  | 0 | 0
1795144 | HPSS 1795144 | 499 | 3 |  | 1549 | 750 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2006 | 21.5 | 39.16 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21.5 |  | 0 | 0
2000418 | HPSS 2000418 | 250 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 8.03% | 1993 | 42 | 39.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
60111 | Inlet 008-R-120 | 499 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 10.99% | NA | 2001 | 21 | 38.99 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21 | 1 | 0 | 21 |  | 1
2001201 | HPSS 2001201 | 250 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1981 | 200.2 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 200.2 |  | 0 | 0
2001347 | HPSS 2001347 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 256.2 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 256.2 |  | 0 | 0
2001369 | HPSS 2001369 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 134.1 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 134.1 |  | 0 | 0
2001537 | HPSS 2001537 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 95.2 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 95.2 |  | 0 | 0
2001660 | HPSS 2001660 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 95.1 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 95.1 |  | 0 | 0
2001752 | HPSS 2001752 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 58.1 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 58.1 |  | 0 | 0
2001773 | HPSS 2001773 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 66.1 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 66.1 |  | 0 | 0
2001783 | HPSS 2001783 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 102.1 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 102.1 |  | 0 | 0
2001246 | HPSS 2001246 | 250 | 3 |  | 1549 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1977 | 57.1 | 38.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.1 |  | 0 | 0
2001785 | HPSS 2001785 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 119.1 | 38.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 119.1 |  | 0 | 0
1795147 | HPSS 1795147 | 499 | 3 |  | 1549 | 720 | 480 | UNKV |  | 480 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2007 | 21 | 38.66 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
1795151 | HPSS 1795151 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1997 | 22.8 | 38.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22.8 |  | 0 | 0
44665 | Inlet 008-R-098 | 250 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1994 | 65.1 | 38.53 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 65.1 | 1 | 0 | 65.1 |  | 1
2000403 | HPSS 2000403 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 49 | 38.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
2001099 | HPSS 2001099 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 83.1 | 38.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 83.1 |  | 0 | 0
2001506 | HPSS 2001506 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 267.9 | 38.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 267.9 |  | 0 | 0
2001664 | HPSS 2001664 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 127 | 38.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 127 |  | 0 | 0
2001671 | HPSS 2001671 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 101.1 | 38.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 101.1 |  | 0 | 0
2001782 | HPSS 2001782 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 57 | 38.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 57 |  | 0 | 0
1577150 | HPSS 1577150 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 111.1 | 38.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 111.1 |  | 0 | 0
2000187 | Service Stub | 250 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 8.03% | 1995 | 57 | 38.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57 |  | 0 | 0
2000084 | HPSS 2000084 | 250 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 8.03% | 1995 | 31 | 38.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31 |  | 0 | 0
31559 | Main Sub | 250 | 3 |  | 1361 | 600 | 400 | 400 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1984 | 154.1 | 38.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 154.1 | 1 | 0 | 154.1 |  | 1
1577120 | HPSS 1577120 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 282.3 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 282.3 |  | 0 | 0
1577156 | HPSS 1577156 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 361.3 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 361.3 |  | 0 | 0
2000138 | HPSS 2000138 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1983 | 277.2 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 277.2 |  | 0 | 0
2000140 | HPSS 2000140 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1983 | 177 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 177 |  | 0 | 0
2000402 | HPSS 2000402 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 82.1 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 82.1 |  | 0 | 0
2001530 | HPSS 2001530 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 122.2 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 122.2 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
2001780 | HPSS 2001780 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 108.1 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 108.1 |  | 0 | 0
2001084 | Service to HPSS 2001078 & 2001103 | 250 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 169.1 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 169.1 |  | 0 | 0
58147 | Inlet 008-R-142 | 250 | 3 |  | 1549 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1999 | 27.1 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 27.1 |  | 0 | 0
2043785 | HPSS 2043785 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 333.3 | 37.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 333.3 |  | 0 | 0
1510052 | Service Stub | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1978 | 86.1 | 37.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 86.1 |  | 0 | 0
2044857 | HPSS 2044857 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1994 | 151.1 | 37.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 151.1 |  | 0 | 0
218419 | Inlet 008-R-134 | 170 | 3 |  | 1193 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 4.27% | NA | 1980 | 28 | 37.77 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 28 |  | 0 | 0
1577140 | HPSS 1577140 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 179.2 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 179.2 |  | 0 | 0
1578400 | HPSS 1578400 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 118.1 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 118.1 |  | 0 | 0
2000129 | HPSS 2000129 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1984 | 144 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 144 |  | 0 | 0
2000132 | HPSS 2000132 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1984 | 139.1 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 139.1 |  | 0 | 0
2001380 | HPSS 2001380 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1984 | 202.2 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 202.2 |  | 0 | 0
2001480 | HPSS 2001480 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 113 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 113 |  | 0 | 0
2001523 | HPSS 2001523 | 250 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1982 | 33 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 33 |  | 0 | 0
2001529 | HPSS 2001529 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 118.1 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 118.1 |  | 0 | 0
2043470 | HPSS 2043470 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 145.1 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 145.1 |  | 0 | 0
2043760 | HPSS 2043760 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 73.1 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 73.1 |  | 0 | 0
2000210 | HPSS 2000210 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1982 | 150.2 | 37.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 150.2 |  | 0 | 0
41108 | Inlet 008-R-041 | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 9.57% | 1992 | 46.5 | 37.07 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 46.5 | 1 | 0 | 46.5 |  | 1
31739 | Inlet 008-R-076 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1984 | 93 | 37.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 93 | 1 | 0 | 93 |  | 1
31628 | Inlet 008-R-069 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1984 | 95.3 | 37.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 95.3 |  | 0 | 0
B0074364 | Inlet 008-R-123 | 499 | 3 |  | 1361 | 760 | 506 | 1440 |  | 506 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 10.99% | 10.99% | 2005 | 16 | 36.99 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 16 | 1 | 0 | 16 |  | 1
45012 | Bangor Naval Submarine Base M&R | 250 | 3 |  | 1001 | 600 | 400 | NA |  | 400 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 9.46% | 9.98% | 1993 | 8.2 | 36.98 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 8.2 | 1 | 0 | 8.2 |  | 1
1577121 | HPSS 1577121 | 250 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1985 | 184.2 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 184.2 |  | 0 | 0
1577155 | HPSS 1577155 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 80.1 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 80.1 |  | 0 | 0
1578406 | HPSS 1578406 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 205.2 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 205.2 |  | 0 | 0
2000139 | HPSS 2000139 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1985 | 183.6 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 183.6 |  | 0 | 0
2000141 | HPSS 2000141 | 250 | 3 |  | 1549 | 110 | 73 | NA |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1983 | 98.1 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 98.1 |  | 0 | 0
2001387 | HPSS 2001387 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 180.2 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 180.2 |  | 0 | 0
2001458 | HPSS 2001464 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1983 | 47 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
2001650 | HPSS 2001650 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 155.2 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 155.2 |  | 0 | 0
2001750 | HPSS 2001750 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 268.3 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 268.3 |  | 0 | 0
2043669 | HPSS 2043669 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 147.1 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 147.1 |  | 0 | 0
2043770 | HPSS 2043770 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 164.2 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 164.2 |  | 0 | 0
2001348 | HPSS 2001348 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 40 | 36.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
1951005 | HPSS 1951005 | 170 | 3 |  | 1549 | 255 | 170 | UNKV |  | 170 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1978 | 34.6 | 36.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.6 |  | 0 | 0
1671126 | HPSS 1671126 | 144 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1979 | 11 | 36.79 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 11 |  | 0 | 0
2043786 | HPSS 2043790 | 250 | 3 |  | 1193 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1994 | 95.1 | 36.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 95.1 |  | 0 | 0
1796011 | HPSS 1796011 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2001 | 31 | 36.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31 |  | 0 | 0
45440 (V-130) | 008-V-130 | 170 | 3 |  | 1106 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 4.61% | 4.61% | 1993 | 21.8 | 36.61 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21.8 |  | 0 | 0
1577130 | HPSS 1577130 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 19.4 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 19.4 |  | 0 | 0
2000137 | HPSS 2000137 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 100.1 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 100.1 |  | 0 | 0
2000469 | HPSS 2000469 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 211.2 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 211.2 |  | 0 | 0
2001070 | HPSS 2001070 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1986 | 106.1 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 106.1 |  | 0 | 0
2001528 | HPSS 2001528 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1984 | 81 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 81 |  | 0 | 0
2043430 | HPSS 2043430 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 93.1 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 93.1 |  | 0 | 0
2043436 | HPSS 2043436 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 175.1 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 175.1 |  | 0 | 0
2000134 | Inlet 008-R-131 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 37 | 36.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 37 |  | 0 | 0
1510049 | HPSS 1510049 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.29% | 3.29% | 1979 | 45 | 36.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
1795152 | HPSS 1795152 | 499 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2002 | 20.2 | 36.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.2 |  | 0 | 0
187456 | 6" Bangor H.P. Line | 250 | 3 |  | 794 | 620 | 413 | 720 |  | 413 | X | X | VALID | 6.625 | 0.188 | 52000 | 0.8 | NO | NO | YES | 8.47% | 12.59% | 2012 | 101.6 | 36.09 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 101.6 | 1 | 0 | 101.6 |  | 1
1577133 | HPSS 1577133 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 124.1 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 124.1 |  | 0 | 0
2000123 | HPSS 2000123 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1985 | 63 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 63 |  | 0 | 0
2000421 | HPSS 2000421 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 43 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
2001203 | HPSS 2001203 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 176.2 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 176.2 |  | 0 | 0
2001204 | HPSS 2001204 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1987 | 262.3 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 262.3 |  | 0 | 0
2001521 | HPSS 2001521 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 67.1 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 67.1 |  | 0 | 0
2043450 | HPSS 2043450 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 93.2 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 93.2 |  | 0 | 0
2043464 | HPSS 2043464 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 66.1 | 35.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 66.1 |  | 0 | 0
1950240 | HPSS 1950240 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1982 | 89.1 | 35.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 89.1 |  | 0 | 0
4423210748 | HPSS 4423210748 | 170 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1984 | 109.1 | 35.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 109.1 |  | 0 | 0
1700260 | HPSS 1700260 | 144 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1981 | 42.2 | 35.79 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 42.2 |  | 0 | 0
23418 | Inlet 008-R-025 | 144 | 3 |  | 1361 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.17% | NA | 1974 | 1.8 | 35.67 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 1.8 |  | 0 | 0
1795150 | HPSS 1795150 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 9.66% | 9.66% | 2003 | 67.7 | 35.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 67.7 |  | 0 | 0
1795153 | HPSS 1795153 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2003 | 33.7 | 35.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 33.7 |  | 0 | 0
35330 | Inlet 008-R-044 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1987 | 19.5 | 35.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 19.5 | 1 | 0 | 19.5 |  | 1
173952 | 2" Belfair H.P. Line | 499 | 3 |  | 1361 | 850 | 566 | 1440 |  | 566 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 10.99% | 10.99% | 2010 | 184.3 | 35.49 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 184.3 |  | 0 | 0
1950847 | Inlet 008-R-111 | 170 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | Service | VALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 3.29% | 5.46% | 1997 | 295 | 35.46 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 295 | 1 | 0 | 295 |  | 1
1577269 | HPSS 1577269 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 120.1 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 120.1 |  | 0 | 0
1577348 | HPSS 1577348 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 118.1 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 118.1 |  | 0 | 0
2000124 | HPSS 2000124 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 103.1 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 103.1 |  | 0 | 0
2000131 | HPSS 2000131 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1988 | 195.2 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 195.2 |  | 0 | 0
2000136 | HPSS 2000136 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 69.1 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 69.1 |  | 0 | 0
2001516 | HPSS 2001516 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1988 | 405 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 405 |  | 0 | 0
2001531 | HPSS 2001531 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 138.1 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 138.1 |  | 0 | 0
2001663 | HPSS 2001663 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 48 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 48 |  | 0 | 0
2001669 | HPSS 2001669 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 135.1 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 135.1 |  | 0 | 0
2001680 | HPSS 2001680 | 250 | 3 |  | 1549 | 125 | 83 | UNKV |  | 83 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 51.4 | 35.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 51.4 |  | 0 | 0
1578403 | HPSS 1578403 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 143.1 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 143.1 |  | 0 | 0
1700304 | HPSS 1700304 | 144 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1982 | 40 | 35.29 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 40 |  | 0 | 0
1795142 | HPSS 1795142 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2004 | 18.4 | 35.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18.4 |  | 0 | 0
60123 | Inlet 008-R-119 | 250 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 2001 | 81.1 | 35.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 81.1 | 1 | 0 | 81.1 |  | 1
35852 | Inlet 008-R-038 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1988 | 10 | 35.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 10 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1578397 | HPSS 1578397 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 120.1 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 120.1 |  | 0 | 0
1578398 | HPSS 1578398 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 150.1 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 150.1 |  | 0 | 0
1578402 | HPSS 1578402 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1989 | 200.3 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 200.3 |  | 0 | 0
2000115 | HPSS 2000115 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 302.3 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 302.3 |  | 0 | 0
2000122 | HPSS 2000122 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 113.1 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 113.1 |  | 0 | 0
2000215 | HPSS 2000235 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 21.8 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21.8 |  | 0 | 0
2000441 | HPSS 2000441 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 89.1 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 89.1 |  | 0 | 0
2001382 | HPSS 2001382 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 117.9 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 117.9 |  | 0 | 0
2001386 | HPSS 2001386 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 104.1 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 104.1 |  | 0 | 0
2001388 | HPSS 2001388 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 100.1 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 100.1 |  | 0 | 0
2001502 | HPSS 2001502 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 238.2 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 238.2 |  | 0 | 0
2001768 | HPSS 2001768 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1989 | 322.3 | 34.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 322.3 |  | 0 | 0
1577264 | HPSS 1577264 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 47 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
2001470 | HPSS 2001470 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 200.2 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 200.2 |  | 0 | 0
1795143 | HPSS 1795143 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2005 | 20.3 | 34.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.3 |  | 0 | 0
52967 | Inlet 008-R-051 | 250 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1997 | 129.2 | 34.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 129.2 | 1 | 0 | 129.2 |  | 1
36728 | Inlet 008-R-060 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1989 | 15.5 | 34.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 15.5 | 1 | 0 | 15.5 |  | 1
37412 | Inlet 008-R-046 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1989 | 93.7 | 34.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 93.7 | 1 | 0 | 93.7 |  | 1
38084 | Main Stub | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1989 | 1 | 34.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1 | 1 | 0 | 1 |  | 1
37000 | Inlet 008-R-054 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1989 | 54.1 | 34.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 54.1 |  | 0 | 0
2000118 | HPSS 2000118 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 195.2 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 195.2 |  | 0 | 0
2000126 | HPSS 2000126 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 66.2 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 66.2 |  | 0 | 0
2001062 | HPSS 2001062 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 239.2 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 239.2 |  | 0 | 0
2001081 | HPSS 2001081 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 100.1 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 100.1 |  | 0 | 0
2001105 | HPSS 2001105 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 264.3 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 264.3 |  | 0 | 0
2001451 | HPSS 2001451 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 103.1 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 103.1 |  | 0 | 0
2001532 | HPSS 2001532 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 158.1 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 158.1 |  | 0 | 0
2001667 | HPSS 2001667 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 80.1 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 80.1 |  | 0 | 0
1578404 | HPSS 1578404 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 25 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
1795146 | HPSS 1795146 | 499 | 3 |  | 1549 | 1080 | 720 | UNKV |  | 720 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2006 | 51 | 34.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
1795160 | HPSS 1795160 | 499 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2006 | 5 | 34.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
53129 | 6" Port Orchard H.P. Loop Line | 170 | 3 |  | 794 | 750 | 500 | NA |  | 500 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 8.56% | 5.75% | 1998 | 469 | 34.06 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 469 | 1 | 0 | 469 |  | 1
39462 | Inlet 008-R-072 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1990 | 67.4 | 34.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 67.4 | 1 | 0 | 67.4 |  | 1
39584 | Inlet 008-R-073 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1990 | 25 | 34.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
41154 | Inlet 008-R-084 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1992 | 108.2 | 34.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 108.2 | 1 | 0 | 108.2 |  | 1
41056 | Inlet 008-R-058 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 119.1 | 34.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 119.1 |  | 0 | 0
1536104 | Service Stub | 170 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.29% | 5.46% | 1998 | 32 | 33.96 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 32 |  | 0 | 0
1577131 | HPSS 1577131 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 128.1 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 128.1 |  | 0 | 0
2000105 | HPSS 2000105 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1991 | 109 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 109 |  | 0 | 0
2000107 | HPSS 2000107 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 101.1 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 101.1 |  | 0 | 0
2000423 | HPSS 2000423 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 104.1 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 104.1 |  | 0 | 0
2000440 | HPSS 2000440 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 115 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 115 |  | 0 | 0
2000443 | HPSS 2000443 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 35.5 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 35.5 |  | 0 | 0
2000600 | HPSS 2000600 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 143.1 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 143.1 |  | 0 | 0
2001202 | HPSS 2001202 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 99.1 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 99.1 |  | 0 | 0
2001340 | HPSS 2001340 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 111.1 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 111.1 |  | 0 | 0
2001389 | HPSS 2001389 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 165 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 165 |  | 0 | 0
2001441 | HPSS 2001441 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 97 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 97 |  | 0 | 0
2001490 | HPSS 2001490 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 217.2 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 217.2 |  | 0 | 0
2001526 | HPSS 2001526 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 238.2 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 238.2 |  | 0 | 0
2001527 | HPSS 2001527 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 164.2 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 164.2 |  | 0 | 0
2001653 | HPSS 2001653 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 48.8 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 48.8 |  | 0 | 0
2001760 | HPSS 2001760 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1989 | 13 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
2043468 | HPSS 2043468 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 133.1 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 133.1 |  | 0 | 0
2000425 | HPSS 2000425 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 125.1 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 125.1 |  | 0 | 0
2001765 | Inlet 008-R-138 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 39 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39 |  | 0 | 0
2001767 | HPSS 2001767 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 281.3 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 281.3 |  | 0 | 0
1795157 | HPSS 1795157 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2007 | 15.3 | 33.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15.3 |  | 0 | 0
1795161 | HPSS 1795161 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 9.66% | 9.66% | 2007 | 26 | 33.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26 |  | 0 | 0
1950816 | HPSS 1950816 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2007 | 15 | 33.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
35998 | Inlet 008-R-047 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1991 | 81 | 33.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 81 | 1 | 0 | 81 |  | 1
39160 | Inlet 008-R-079 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1991 | 10 | 33.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 10 | 1 | 0 | 10 |  | 1
1578401 | Inlet 008-R-133 | 250 | 3 |  | 1549 | 90 | 60 | 1440 |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1990 | 70.2 | 33.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 70.2 |  | 0 | 0
2000117 | HPSS 2000117 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 31 | 33.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 31 |  | 0 | 0
2000121 | HPSS 2000121 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 52 | 33.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
2000457 | HPSS 2000457 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 93.1 | 33.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 93.1 |  | 0 | 0
2001078 | HPSS 2001078 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1992 | 162.2 | 33.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 162.2 |  | 0 | 0
2001786 | HPSS 2001786 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 133 | 33.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 133 |  | 0 | 0
175967 | Inlet 008-R-143 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1988 | 42 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
2000116 | HPSS 2000116 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 226 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 226 |  | 0 | 0
2044927 | HPSS 2044927 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2001 | 40.2 | 33.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.2 |  | 0 | 0
1795154 | HPSS 1795154 | 499 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 2008 | 35.7 | 33.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35.7 |  | 0 | 0
41028 | Inlet 008-R-044 | 250 | 3 |  | 1361 | 600 | 400 | 720 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 61.9 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 61.9 | 1 | 0 | 61.9 |  | 1
41030 | Inlet 008-R-045 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 16.3 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 16.3 | 1 | 0 | 16.3 |  | 1
41032 | Inlet 008-R-046 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 22.7 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 22.7 | 1 | 0 | 22.7 |  | 1
41034 | Inlet 008-R-047 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 12 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 12 | 1 | 0 | 12 |  | 1
41040 | Inlet 008-R-050 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 18 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 18 | 1 | 0 | 18 |  | 1
43557 | Inlet 008-R-096 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1994 | 125.3 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 125.3 | 1 | 0 | 125.3 |  | 1
45087 | Inlet 008-R-099 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1994 | 104.2 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 104.2 | 1 | 0 | 104.2 |  | 1
41049 | Inlet 008-R-055 | 250 | 3 |  | 1361 | 600 | 400 | NA |  | 400 | X | X | VALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NO | YES | 3.32% | 5.51% | 1992 | 12.5 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 12.5 | 1 | 0 | 12.5 |  | 1
41038 | Inlet 008-R-049 | 250 | 3 |  | 1361 | 600 | 400 | 720 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 20 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20 | 1 | 0 | 20 |  | 1
41313 | Inlet 008-R-085 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1992 | 56 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 56 | 1 | 0 | 56 |  | 1
41347 | Inlet 008-R-086 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1992 | 18.7 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 18.7 | 1 | 0 | 18.7 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
41971 | Inlet 008-R-087 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1992 | 22.2 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 22.2 | 1 | 0 | 22.2 |  | 1
42141 | Inlet 008-R-089 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1992 | 31.2 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 31.2 | 1 | 0 | 31.2 |  | 1
42392 | Inlet 008-R-091 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 26 | 33.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 26 | 1 | 0 | 26 |  | 1
41073 | Inlet 008-R-066 | 250 | 3 |  | 1361 | 600 | 400 | UNKV |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NO | YES | 5.51% | 5.51% | 1992 | 10.3 | 33.01 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10.3 |  | 0 | 0
41036 | Inlet 008-R-048 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 64.1 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 64.1 |  | 0 | 0
41046 | Inlet 008-R-053 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 13.5 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 13.5 |  | 0 | 0
41048 | Inlet 008-R-054 | 250 | 3 |  | 1361 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 11 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 11 |  | 0 | 0
41052 | Inlet 008-R-056 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 17.4 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 17.4 |  | 0 | 0
41054 | Inlet 008-R-057 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 24.2 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 24.2 |  | 0 | 0
41058 | Inlet 008-R-059 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 10 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 10 |  | 0 | 0
41062 | Inlet 008-R-061 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 36 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 36 |  | 0 | 0
41064 | Inlet 008-R-062 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 7 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 7 |  | 0 | 0
41066 | Inlet 008-R-063 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 14.1 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.1 |  | 0 | 0
41079 | Inlet 008-R-069 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 36 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 36 |  | 0 | 0
41083 | Inlet 008-R-071 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 24 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 24 |  | 0 | 0
41085 | Inlet 008-R-072 | 250 | 3 |  | 1361 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 38.9 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 38.9 |  | 0 | 0
41087 | Inlet 008-R-073 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 22.5 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 22.5 |  | 0 | 0
41094 | Inlet 008-R-076 | 250 | 3 |  | 1361 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 5.3 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 5.3 |  | 0 | 0
41096 | Inlet 008-R-148 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 15.5 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 15.5 |  | 0 | 0
41100 | Inlet 008-R-079 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 14 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14 |  | 0 | 0
41104 | Inlet 008-R-081 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 33 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 33 |  | 0 | 0
41060 | Inlet 008-R-060 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 3 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 3 |  | 0 | 0
41071 | Inlet 008-R-065 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 32.5 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 32.5 |  | 0 | 0
41075 | Inlet 008-R-067 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 2 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 2 |  | 0 | 0
41089 | Inlet 008-R-074 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1992 | 12 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 12 |  | 0 | 0
1577152 | HPSS 1577152 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 183.2 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 183.2 |  | 0 | 0
1578396 | HPSS 1578396 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 40 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
1578408 | HPSS 1578408 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1991 | 43 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
2000110 | HPSS 2000110 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 63.1 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 63.1 |  | 0 | 0
2000111 | HPSS 2000111 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 70 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 70 |  | 0 | 0
2000113 | HPSS 2000113 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 35 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
2000422 | HPSS 2000422 | 250 | 3 |  | 1549 | 100 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1991 | 12 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
2001117 | HPSS 2001117 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1991 | 35 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
2001456 | HPSS 2001456 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 64.1 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 64.1 |  | 0 | 0
2001534 | HPSS 2001534 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 65.1 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 65.1 |  | 0 | 0
2001536 | HPSS 2001536 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1991 | 40 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
2001668 | HPSS 2001668 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 85 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 85 |  | 0 | 0
2001670 | HPSS 2001670 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 98.1 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 98.1 |  | 0 | 0
2001791 | HPSS 2001791 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 50.1 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 50.1 |  | 0 | 0
2001517 | HPSS 2001517 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 14 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
2001751 | HPSS 2001751 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 63.1 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 63.1 |  | 0 | 0
2043451 | HPSS 2043451 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 113.2 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 113.2 |  | 0 | 0
45440 (V-128) | 008-V-128 | 170 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.81% | 4.61% | 1993 | 4 | 32.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4 | 1 | 0 | 4 |  | 1
49712 | 6" Port Orchard H.P. Loop Line (Inlet to 008-R-109) | 170 | 3 |  | 877 | 860 | 573 | 720 |  | 573 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 5.81% | NA | 1995 | 426.4 | 32.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 426.4 | 1 | 0 | 426.4 |  | 1
1510048 | HPSS 1510048 | 170 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.29% | 3.29% | 1986 | 24.9 | 32.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24.9 |  | 0 | 0
1700806 | HPSS 1700806 | 144 | 3 |  | 1549 | 225 | 150 | UNKV |  | 150 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1985 | 52 | 32.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
44659 | Inlet 008-R-074 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1993 | 14.2 | 32.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.2 |  | 0 | 0
1577292 | HPSS 1577292 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 113.1 | 32.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 113.1 |  | 0 | 0
2000199 | HPSS 2000199 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 81.1 | 32.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 81.1 |  | 0 | 0
1577200 | HPSS 1577200 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 28 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 28 |  | 0 | 0
2000409 | HPSS 2000409 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 255.2 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 255.2 |  | 0 | 0
2000424 | HPSS 2000424 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 102 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 102 |  | 0 | 0
2001101 | HPSS 2001101 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 40 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
2001459 | HPSS 2001459 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1992 | 122.1 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 122.1 |  | 0 | 0
2001519 | HPSS 2001519 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 85 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 85 |  | 0 | 0
2001538 | HPSS 2001538 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 146.1 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 146.1 |  | 0 | 0
2001541 | HPSS 2001541 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 237.3 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 237.3 |  | 0 | 0
2001547 | HPSS 2001547 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1992 | 205.1 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 205.1 |  | 0 | 0
2001753 | HPSS 2001753 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 158.2 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 158.2 |  | 0 | 0
218304 | Inlet 008-R-137 | 250 | 3 |  | 1549 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1990 | 54 | 32.34 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 54 |  | 0 | 0
47657 | Inlet 008-R-032 | 170 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.81% | 4.61% | 1994 | 10.6 | 32.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 10.6 |  | 0 | 0
7722217496 | HPSS 7722217496 | 250 | 3 |  | 1193 | 94 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 6.28% | 4.84% | 2013 | 25 | 32.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
46593 | Inlet 008-R-103 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1994 | 28 | 32.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 28 | 1 | 0 | 28 |  | 1
2000184 | HPSS 2000184 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 217.2 | 31.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 217.2 |  | 0 | 0
1577212 | HPSS 1577212 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 157 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 157 |  | 0 | 0
1578399 | HPSS 1578399 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 14 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
1578416 | HPSS 1578416 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 219.2 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 219.2 |  | 0 | 0
1700752 | HPSS 1700752 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 119.1 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 119.1 |  | 0 | 0
2001390 | HPSS 2001390 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1993 | 164.2 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 164.2 |  | 0 | 0
2001453 | HPSS 2001453 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1993 | 206.2 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 206.2 |  | 0 | 0
2001544 | HPSS 2001544 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 210.2 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 210.2 |  | 0 | 0
2043469 | HPSS 2043469 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 149.1 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 149.1 |  | 0 | 0
1950948 | Service Stub | 170 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | NA | NA | NA | NA | YES | YES | YES | NA | 3.29% | 1990 | 15 | 31.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
1510083 | HPSS 1510083 | 170 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1990 | 35 | 31.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
1700321 | HPSS 1700321 | 144 | 3 |  | 1549 | 95 | 63 | UNKV |  | 63 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1991 | 140.1 | 31.79 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 140.1 |  | 0 | 0
1700438 | HPSS 1700438 | 144 | 3 |  | 1549 | 225 | 150 | UNKV |  | 150 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1987 | 29 | 31.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29 |  | 0 | 0
3671839373 | HPSS 3671839373 | 250 | 3 |  | 1193 | 760 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2014 | 17 | 31.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
49477 | Inlet 008-R-108 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1995 | 19.4 | 31.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 19.4 | 1 | 0 | 19.4 |  | 1
48279 | Inlet 008-R-105 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1995 | 25 | 31.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
218305 | Inlet 008-R-130 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1992 | 51.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51.1 |  | 0 | 0
1571100 | HPSS 1571100 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 105 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 105 |  | 0 | 0
1577280 | HPSS 1577280 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 154.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 154.1 |  | 0 | 0
1578356 | HPSS 1578356 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 106.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 106.1 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1578394 | HPSS 1578394 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 145.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 145.1 |  | 0 | 0
2000100 | HPSS 2000100 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 245.2 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 245.2 |  | 0 | 0
2000158 | HPSS 2000158 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 96 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 96 |  | 0 | 0
2000174 | HPSS 2000174 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1992 | 36.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36.1 |  | 0 | 0
2000411 | HPSS 2000411 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 110.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 110.1 |  | 0 | 0
2001093 | HPSS 2001093 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 95.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 95.1 |  | 0 | 0
2001352 | HPSS 2001352 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 175.2 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 175.2 |  | 0 | 0
2001514 | HPSS 2001514 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 70.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 70.1 |  | 0 | 0
2001515 | HPSS 2001515 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 89.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 89.1 |  | 0 | 0
2001545 | HPSS 2001545 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 113.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 113.1 |  | 0 | 0
1510085 | HPSS 1510085 | 170 | 3 |  | 1549 | 95 | 63 | UNKV |  | 63 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1991 | 90.1 | 31.29 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 90.1 |  | 0 | 0
1700442 | Service Stub | 144 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.79% | NA | 1990 | 3 | 31.29 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 3 |  | 0 | 0
1700262 | HPSS 1700262 | 144 | 3 |  | 1549 | 95 | 63 | UNKV |  | 63 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1990 | 34 | 31.29 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 34 |  | 0 | 0
1700441 | HPSS 1700441 | 144 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1988 | 25 | 31.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
33923 | Stub on Inlet 008-R-035 | 170 | 3 |  | 1361 | 400 | 1 | 1440 |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.75% | NA | 1986 | 181.8 | 31.25 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 181.8 |  | 0 | 0
B0080173 | 8" North Kitsap H.P. Line | 250 | 3 |  | 1045 | 681 | 454 | 720 |  | 454 | X |  | UNVALID | 8.625 | 0.25 | 46000 | 0.8 | NO | NO | YES | 9.38% | 9.57% | 2006 | 118.1 | 31.07 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 118.1 |  | 0 | 0
2000095 | HPSS 2000095 | 250 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1995 | 42.2 | 30.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 42.2 |  | 0 | 0
1571106 | HPSS 1571106 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 128.4 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 128.4 |  | 0 | 0
1577279 | HPSS 1577279 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 56.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56.1 |  | 0 | 0
1578417 | HPSS 1578417 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 26 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26 |  | 0 | 0
1578428 | HPSS 1578428 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 111.2 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 111.2 |  | 0 | 0
2000082 | HPSS 2000082 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 199.2 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 199.2 |  | 0 | 0
2000148 | HPSS 2000148 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 77.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77.1 |  | 0 | 0
2000177 | HPSS 2000177 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1993 | 72.4 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 72.4 |  | 0 | 0
2000207 | HPSS 2000207 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 125.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 125.1 |  | 0 | 0
2000416 | HPSS 2000416 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 193.2 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 193.2 |  | 0 | 0
2000419 | HPSS 2000419 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1993 | 77.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77.1 |  | 0 | 0
2000420 | HPSS 2000420 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 108 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 108 |  | 0 | 0
2000430 | HPSS 2000430 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 123.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 123.1 |  | 0 | 0
2001391 | HPSS 2001391 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 42 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
2001443 | HPSS 2001443 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 111.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 111.1 |  | 0 | 0
2001504 | HPSS 2001504 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 103.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 103.1 |  | 0 | 0
2001513 | HPSS 2001513 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 22 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
2001543 | HPSS 2001543 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 130 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 130 |  | 0 | 0
2001682 | HPSS 2001682 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 116.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 116.1 |  | 0 | 0
2001695 | HPSS 2001695 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 22 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
2001799 | HPSS 2001799 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 65 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 65 |  | 0 | 0
2043439 | HPSS 2043439 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 146.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 146.1 |  | 0 | 0
2043671 | HPSS 2043671 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 190.2 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 190.2 |  | 0 | 0
1951004 | HPSS 1951004 | 170 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1990 | 13.3 | 30.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13.3 |  | 0 | 0
1700285 | HPSS 1700285 | 144 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1991 | 30 | 30.79 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 30 |  | 0 | 0
1700423 | HPSS 1700423 | 144 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 2.79% | 1991 | 135 | 30.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 135 |  | 0 | 0
2001908 | HPSS 2001908 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 15 | 30.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
1571108 | HPSS 1571108 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 37 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 37 |  | 0 | 0
1571105 | HPSS 1571119 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 13.8 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13.8 |  | 0 | 0
1577136 | Inlet 008-R-135 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 167.2 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 167.2 |  | 0 | 0
2000098 | HPSS 2000098 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 76.1 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 76.1 |  | 0 | 0
2000468 | HPSS 2000468 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1994 | 85 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 85 |  | 0 | 0
2001032 | HPSS 2001032 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 38 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
2001353 | HPSS 2001353 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 15 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
2001552 | HPSS 2001552 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 63 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 63 |  | 0 | 0
2001801 | HPSS 2001801 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 89.1 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 89.1 |  | 0 | 0
1950972 | Service Stub | 170 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1991 | 50.1 | 30.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50.1 |  | 0 | 0
1950974 | Service Stub | 170 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1991 | 1 | 30.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1 |  | 0 | 0
1700322 | HPSS 1700322 | 144 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1990 | 17.1 | 30.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17.1 |  | 0 | 0
54835 | Inlet 008-R-116 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1998 | 21 | 30.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21 | 1 | 0 | 21 | 1
B0080224 | Inlet 008-R-124 | 170 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 5.46% | 5.46% | 2006 | 89.2 | 29.96 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 89.2 |  | 0 | 0
1571115 | HPSS 1571115 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 44 | 29.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
2000446 | HPSS 2000446 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 25 | 29.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
1571113 | HPSS 1571113 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 263.3 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 263.3 |  | 0 | 0
1571437 | HPSS 1571437 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 18.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18.1 |  | 0 | 0
1578424 | HPSS 1578424 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 44 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
1578438 | HPSS 1578438 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 44 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
1700668 | HPSS 1700668 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 82.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 82.1 |  | 0 | 0
1700759 | HPSS 1700759 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 90.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 90.1 |  | 0 | 0
1700761 | HPSS 1700761 | 250 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 80.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 80.1 |  | 0 | 0
201253 | Inlet 008-R-151 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 56.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56.1 |  | 0 | 0
2000102 | HPSS 2000102 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1997 | 149.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 149.1 |  | 0 | 0
2000180 | HPSS 2000180 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 14.9 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14.9 |  | 0 | 0
2000181 | HPSS 2000181 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 52 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
2000183 | HPSS 2000183 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 30.2 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30.2 |  | 0 | 0
2000186 | HPSS 2000186 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 40.9 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.9 |  | 0 | 0
2000189 | HPSS 2000189 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1997 | 254.3 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 254.3 |  | 0 | 0
2000444 | HPSS 2000444 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 58 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
2001907 | HPSS 2001907 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 93.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 93.1 |  | 0 | 0
2043466 | HPSS 2043466 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 61.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 61.1 |  | 0 | 0
1510086 | HPSS 1510086 | 170 | 3 |  | 1549 | 730 | 486 | UNKV |  | 486 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1994 | 100 | 29.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 100 |  | 0 | 0
1510088 | HPSS 1510088 | 170 | 3 |  | 1549 | 730 | 486 | UNKV |  | 486 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1994 | 111.2 | 29.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 111.2 |  | 0 | 0
1510100 | HPSS 1510100 | 170 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1992 | 40 | 29.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
1700673 | HPSS 1700673 | 144 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.79% | 2.79% | 1993 | 145.1 | 29.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 145.1 |  | 0 | 0
2000192 | HPSS 2000192 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 33 | 29.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 33 |  | 0 | 0
2001474 | HPSS 2001474 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 55.1 | 29.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
1574506 | HPSS 1574506 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 24 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1578481 | HPSS 1578481 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 42.9 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.9 |  | 0 | 0
2001373 | HPSS 2001373 | 250 | 3 |  | 1549 | 760 | 506 | UNKV |  | 506 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 39.1 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39.1 |  | 0 | 0
2001553 | HPSS 2001553 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 16 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
2001675 | HPSS 2001675 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 49 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
2043461 | HPSS 2043461 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 32 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 32 |  | 0 | 0
2043672 | HPSS 2043672 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 8 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
1510027 | HPSS 1510027 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1993 | 19 | 29.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
1950970 | HPSS 1950970 | 170 | 3 |  | 1549 | 760 | 506 | UNKV |  | 506 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1993 | 48.4 | 29.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48.4 |  | 0 | 0
1700286 | HPSS 1700286 | 144 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1992 | 40 | 29.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
2001813 | HPSS 2001813 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 51 | 28.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
1571107 | HPSS 1571107 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 14 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
1577213 | HPSS 1577213 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 16 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
1577295 | HPSS 1577295 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 11 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
1578505 | HPSS 1578505 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 50.9 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50.9 |  | 0 | 0
1579268 | HPSS 1579268 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 55.1 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
2000214 | HPSS 2000214 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 14 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
2000426 | HPSS 2000426 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 27 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 27 |  | 0 | 0
2000431 | HPSS 2000431 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 41 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41 |  | 0 | 0
2000432 | HPSS 2000432 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 17 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
2001379 | HPSS 2001379 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 45 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
2001449 | HPSS 2001449 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 68.1 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 68.1 |  | 0 | 0
2001466 | HPSS 2001466 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 43 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
2001500 | HPSS 2001500 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 54 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
2001512 | HPSS 2001512 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 30.1 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30.1 |  | 0 | 0
2001554 | HPSS 2001554 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 11 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
2001555 | HPSS 2001555 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 35 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
2001657 | HPSS 2001657 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1997 | 51.3 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51.3 |  | 0 | 0
2001661 | HPSS 2001661 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 14 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
2043471 | HPSS 2043471 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 16 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
1510002 | HPSS 1510002 | 170 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1996 | 18 | 28.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
1510134 | HPSS 1510134 | 170 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1996 | 12.9 | 28.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12.9 |  | 0 | 0
1510135 | HPSS 1510135 | 170 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1996 | 12.9 | 28.79 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12.9 |  | 0 | 0
1510130 | HPSS 1510130 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1996 | 160.1 | 28.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 160.1 |  | 0 | 0
1671085 | HPSS 1671085 | 144 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1993 | 70.1 | 28.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 70.1 |  | 0 | 0
1571117 | HPSS 1571117 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 22 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
1578494 | HPSS 1578494 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 16 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
2000218 | HPSS 2000218 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 34.1 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.1 |  | 0 | 0
2001666 | HPSS 2001666 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 46 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
1700327 | HPSS 1700327 | 144 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1994 | 34 | 28.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34 |  | 0 | 0
366665439 | HPSS 366665439 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2011 | 55 | 28.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
6202304978 | HPSS 6202304978 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2011 | 29.1 | 28.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29.1 |  | 0 | 0
9341211532 | HPSS 9341211532 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2011 | 45 | 28.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
35162 | Inlet 008-R-036 | 170 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.75% | NA | 1988 | 18 | 28.25 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 18 |  | 0 | 0
B0072657 | Inlet 008-R-126 | 499 | 3 |  | 2260 | 1000 | 666 | 1440 |  | 666 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NO | YES | 6.62% | 5.24% | 2004 | 11.6 | 28.12 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 11.6 |  | 0 | 0
2000429 | HPSS 2000429 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2001 | 21 | 27.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
1571438 | HPSS 1571438 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 10.1 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10.1 |  | 0 | 0
1578502 | HPSS 1578502 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 49 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
1578506 | HPSS 1578506 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 73.1 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 73.1 |  | 0 | 0
1670010 | HPSS 1670010 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 56 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56 |  | 0 | 0
2000221 | HPSS 2000221 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1999 | 64.1 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 64.1 |  | 0 | 0
1510131 | HPSS 1510131 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1996 | 20.9 | 27.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.9 |  | 0 | 0
2127970167 | HPSS 2127970167 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2012 | 60 | 27.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60 |  | 0 | 0
4190389931 | HPSS 4190389931 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2012 | 43 | 27.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
9243868169 | HPSS 9243868169 | 250 | 3 |  | 1214 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 6.18% | NA | 2012 | 60 | 27.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60 |  | 0 | 0
B0074106 | Inlet 008-R-125 | 499 | 3 |  | 2260 | 760 | 506 | 1440 |  | 506 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 6.62% | NA | 2005 | 17 | 27.62 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 17 |  | 0 | 0
2000086 | HPSS 2000086 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 34 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34 |  | 0 | 0
2000151 | HPSS 2000151 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 34.1 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.1 |  | 0 | 0
2001558 | HPSS 2001558 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 28.1 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 28.1 |  | 0 | 0
2001560 | HPSS 2001560 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 77 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77 |  | 0 | 0
2001911 | HPSS 2001911 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 60.1 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60.1 |  | 0 | 0
2043441 | HPSS 2043441 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 21.1 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21.1 |  | 0 | 0
1950977 | HPSS 1950977 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1997 | 76.4 | 27.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 76.4 |  | 0 | 0
1700289 | HPSS 1700348 | 144 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1996 | 24 | 27.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24 |  | 0 | 0
1700439 | HPSS 1700439 | 144 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1996 | 50.1 | 27.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50.1 |  | 0 | 0
4304310213 | HPSS 2043645 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2013 | 94 | 27.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 94 |  | 0 | 0
2350437741 | HPSS 2350437741 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2013 | 46 | 27.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
5634302764 | HPSS 5634302764 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2013 | 40 | 27.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
B0078745 | Inlet 008-R-128 | 499 | 3 |  | 2260 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 6.62% | NA | 2006 | 26 | 27.12 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 26 |  | 0 | 0
209032 | 6" North Bremerton H.P. Line | 250 | 3 |  | 1056 | 638 | 425 | 720 |  | 425 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 9.46% | 5.69% | 2014 | 279.9 | 26.96 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 279.9 | 1 | 0 | 279.9 |  | 1
2001508 | HPSS 2001508 | 250 | 3 |  | 1549 | 750 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 159.4 | 26.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 159.4 |  | 0 | 0
1578437 | HPSS 1578437 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2001 | 59.1 | 26.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 59.1 |  | 0 | 0
1578517 | HPSS 1578517 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2001 | 46 | 26.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
2000229 | HPSS 2000229 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2001 | 44 | 26.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
2000256 | HPSS 2000256 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2001 | 13 | 26.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
2000448 | HPSS 2000448 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2001 | 30 | 26.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
1510136 | HPSS 1510136 | 170 | 3 |  | 1549 | 770 | 513 | UNKV |  | 513 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1998 | 23.9 | 26.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.9 |  | 0 | 0
1536103 | HPSS 1536103 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1998 | 8 | 26.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
1536106 | HPSS 1536106 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1998 | 22 | 26.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
1536105 | Service Stub | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1998 | 52.7 | 26.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52.7 |  | 0 | 0
2737238005 | HPSS 2737238005 | 250 | 3 |  | 1193 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2014 | 17 | 26.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
8710281410 | HPSS 8710281410 | 250 | 3 |  | 1193 | 780 | 520 | UNKV |  | 520 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2014 | 32.1 | 26.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 32.1 |  | 0 | 0
8870699770 | HPSS 8870699770 | 250 | 3 |  | 1214 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 6.18% | NA | 2014 | 59 | 26.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 59 |  | 0 | 0
41094 (V-001) | 008-V-001 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X |  | UNVALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1984 | 0 | 26.5 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
1578518 | HPSS 1578518 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 21 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
2001031 | HPSS 2001031 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 42 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
2001672 | HPSS 2001672 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 24.1 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24.1 |  | 0 | 0
2043445 | HPSS 2043445 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 55.1 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
1510362 | HPSS 1510362 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 1999 | 59.1 | 26.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 59.1 |  | 0 | 0
1700437 | HPSS 1700437 | 144 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.79% | NA | 1998 | 8 | 26.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
7945724317 | HPSS 7945724317 | 250 | 3 |  | 1193 | 799 | 532 | UNKV |  | 532 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2015 | 30 | 26.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
7946173702 | HPSS 7946173702 | 250 | 3 |  | 1193 | 760 | 506 | UNKV |  | 506 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2015 | 51 | 26.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
210812 | 8" North Kitsap H.P. Line | 250 | 3 |  | 1183 | 660 | 440 | 720 |  | 440 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 8.29% | 8.45% | 2014 | 107.7 | 25.95 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 107.7 | 1 | 0 | 107.7 |  | 1
2001556 | HPSS 2001556 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 52 | 25.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
1578803 | HPSS 1578803 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 16 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
2001251 | Inlet 008-R-132 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 57.1 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.1 |  | 0 | 0
1950254 | HPSS 1950254 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 2000 | 56.1 | 25.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56.1 |  | 0 | 0
49714 | Inlet 008-R-109 | 170 | 3 |  | 1106 | 750 | 500 | NA |  | 500 | X |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NA | NA | 4.61% | NA | 1995 | 6 | 25.61 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 6 |  | 0 | 0
228923 | Inlet 008-R-156 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2004 | 20.1 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.1 |  | 0 | 0
1577218 | HPSS 1577218 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 289 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 289 |  | 0 | 0
1950150 | HPSS 1950150 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 2001 | 50.7 | 25.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50.7 |  | 0 | 0
45247 | Inlet 008-R-101 | 170 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.75% | NA | 1994 | 67.7 | 25.25 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 67.7 | 1 | 0 | 67.7 |  | 1
50949 | Inlet 008-R-035 | 170 | 3 |  | 1106 | 750 | 500 | NA |  | 500 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NA | NA | 4.61% | NA | 1996 | 5.9 | 25.11 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5.9 | 1 | 0 | 5.9 |  | 1
1571123 | HPSS 1571123 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2007 | 199.2 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 199.2 |  | 0 | 0
2001433 | HPSS 2001433 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 19 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
2001565 | HPSS 2001565 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 84.1 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 84.1 |  | 0 | 0
2043467 | HPSS 2043467 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 29 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29 |  | 0 | 0
2043472 | HPSS 2043472 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 55.1 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
1510147 | HPSS 1510147 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 2002 | 42.1 | 24.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.1 |  | 0 | 0
47827 | Inlet 008-R-104 | 170 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.75% | 3.75% | 1995 | 65.1 | 24.75 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 65.1 | 1 | 0 | 65.1 |  | 1
47828 | Inlet 008-R-104 | 170 | 3 |  | 1361 | 600 | 400 | NA |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.75% | NA | 1995 | 6 | 24.75 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6 | 1 | 0 | 6 |  | 1
1571122 | HPSS 1571122 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 12 | 24.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
1577302 | HPSS 1577302 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 27 | 24.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 27 |  | 0 | 0
2001038 | HPSS 2001038 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 55.1 | 24.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
2000406 | Inlet 008-R-137 | 250 | 3 |  | 1549 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | NA | NA | NA | NA | NO | YES | YES | NA | 4.84% | 2006 | 0 | 24.34 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
50951 | Inlet 008-R-035 | 170 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.75% | 3.75% | 1996 | 20.8 | 24.25 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20.8 | 1 | 0 | 20.8 |  | 1
49794 | Inlet 008-R-110 | 170 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.75% | NA | 1996 | 69.1 | 24.25 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 69.1 | 1 | 0 | 69.1 |  | 1
53132 | Inlet 008-R-113 | 170 | 3 |  | 1106 | 750 | 500 | NA |  | 500 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NA | NA | 4.61% | NA | 1998 | 2.5 | 24.11 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2.5 | 1 | 0 | 2.5 |  | 1
1571439 | HPSS 1571439 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2007 | 14.1 | 23.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14.1 |  | 0 | 0
2041172 | HPSS 2041172 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2009 | 347.3 | 23.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 347.3 |  | 0 | 0
174704 | Inlet 008-R-144 | 499 | 3 |  | 3539 | 750 | 500 | 720 |  | 500 | X | X | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NA | NA | 7.05% | NA | 2010 | 4 | 23.55 | No Action Needed | -- | 1 | 1 | 0 | 4 | 1 | 0 | 4 |  | 1
1578510 | HPSS 1578510 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2008 | 15.2 | 23.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15.2 |  | 0 | 0
54728 | Inlet 008-R-115 | 170 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.75% | 3.75% | 1998 | 58.1 | 23.25 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 58.1 |  | 0 | 0
1570006 | HPSS 1570006 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2010 | 16 | 22.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
178845 | Inlet 008-R-145 | 250 | 3 |  | 1549 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | NO | YES | YES | 3.53% | 4.84% | 2010 | 15 | 22.34 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 15 |  | 0 | 0
1536111 | HPSS 1536111 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 2007 | 20 | 22.29 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
1950848 | HPSS 1950848 | 170 | 3 |  | 2260 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 2.26% | NA | 1999 | 47 | 22.26 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
209777 | Inlet 008-R-070 | 250 | 3 |  | 1361 | 770 | 513 | 720 |  | 513 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2014 | 80.4 | 22.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 80.4 | 1 | 0 | 80.4 |  | 1
234385 | Inlet 008-R-047 | 250 | 3 |  | 1361 | 400 | 266 | 720 |  | 266 | X | X | VALID | 2.375 | 0.154 | 52000 | 0.6 | NO | NO | YES | 3.71% | 5.51% | 2016 | 116.2 | 22.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 116.2 | 1 | 0 | 116.2 |  | 1
226327 | Inlet 008-R-155 | 250 | 3 |  | 1361 | 640 | 426 | 720 |  | 426 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2016 | 59 | 21.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 59 | 1 | 0 | 59 |  | 1
1571119 | HPSS 1571119 | 250 | 3 |  | 2260 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2002 | 34 | 20.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34 |  | 0 | 0
1536109 | HPSS 1536109 | 170 | 3 |  | 2260 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 2.26% | NA | 2000 | 19 | 20.76 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
50200 | 12" Kitsap H.P. Line | 499 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1996 | 0 | 20.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
51144 | 4" Port Orchard H.P. Line (008-V-161) | 170 | 3 |  | NA | NA | NA | 1440 |  | 1440 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1996 | 0 | 20.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
2168154319 | HPSS 2168154319 | 144 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.62% | NA | 2012 | 34 | 20.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34 |  | 0 | 0
1477210777 | HPSS 1477210777 | 250 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2015 | 71 | 19.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 71 |  | 0 | 0
4929900230 | HPSS 1510025 | 170 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.29% | NA | 2016 | 13.1 | 17.79 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13.1 |  | 0 | 0
163400 | Inlet 008-R-141 | 144 | 3 |  | 1361 | 650 | 433 | 720 |  | 433 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.17% | NA | 2009 | 82.6 | 17.17 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 82.6 | 1 | 0 | 82.6 |  | 1
1951002 | Inlet 008-R-134 | 170 | 3 |  | NA | NA | NA | 275 |  | 275 | X |  | UNVALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2004 | 0 | 16.5 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
186169 | Inlet 008-R-150 | 175 | 3 |  | 1361 | 375 | 250 | 720 |  | 250 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.86% | 3.86% | 2012 | 47 | 16.36 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 47 | 1 | 0 | 47 |  | 1
186076 | Inlet 008-R-149 | 250 | 3 |  | 3539 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NA | NA | 3.53% | NA | 2011 | 2 | 14.53 | No Action Needed | -- | 1 | 1 | 0 | 2 | 1 | 0 | 2 |  | 1
198153 | Inlet 008-R-147 | 170 | 3 |  | 2123 | 750 | 500 | 720 |  | 500 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NO | YES | 2.40% | 2.40% | 2013 | 41 | 14.4 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 41 | 1 | 0 | 41 |  | 1
2777116375 | HPSS 2777116375 | 250 | 3 |  | 2123 | 765 | 510 | UNKV |  | 510 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 3.53% | NA | 2016 | 34 | 14.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34 |  | 0 | 0
9586322241 | HPSS 9586322241 | 144 | 3 |  | 2123 | 765 | 510 | 720 |  | 510 | X | Service | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 2.03% | NA | 2014 | 14 | 13.53 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 14 | 1 | 0 | 14 |  | 1
2231864471 | HPSS 2231864471 | 144 | 3 |  | 2123 | 798 | 532 | UNKV |  | 532 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 2.03% | NA | 2015 | 41 | 13.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41 |  | 0 | 0
186074 | Inlet 008-R-148 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2011 | 0 | 13 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
186070 | Inlet 008-R-063 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X |  | UNVALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2011 | 0 | 13 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
3362513977 | HPSS 3362513977 | 250 | 3 |  | 3539 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 1 | YES | NA | NA | 3.53% | NA | 2017 | 20 | 11.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
4558360240 | HPSS 4558360240 | 250 | 3 |  | 3539 | 712 | 474 | UNKV |  | 474 | X | Service | UNVALID | 1.315 | 0.133 | 42000 | 1 | YES | NO | NO | 2.94% | 3.53% | 2017 | 21 | 11.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
2460572735 | HPSS 2460572735 | 170 | 3 |  | 3539 | 720 | 480 | UNKV |  | 480 | X | Service | UNVALID | 1.315 | 0.133 | 42000 | 1 | YES | NO | NO | 2.00% | 2.40% | 2017 | 14 | 10.4 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
01C4776 | 8"Attalia Transmission Line | 300 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 28.67% | 7.54% | 1958 | 79269 | 168.17 | 116 Segment, Pressure Test | 2021 | 1 | 0 | 79269 | 0 |  | 0 | 0
01C4776 | 8"Attalia Transmission Line | 300 | 3 |  | 418 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NO | YES | 28.67% | 11.48% | 1958 | 76.5 | 143.17 | 116 Segment, Pressure Test | 2021 | 1 | 0 | 76.5 | 0 |  | 0 | 0
53C2527 | 4" Finley H.P. Line | 200 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 12.02% | NA | 1959 | 10328.7 | 108.02 | 116 Segment, Pressure Test | 2020 | 1 | 0 | 10328.7 | 0 |  | 0 | 0
54C2565 | Inlet 023-R-006 | 300 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 9.64% | 9.64% | 1959 | 2 | 84.14 | 116 Segment, Replace | 2021 | 1 | 0 | 2 | 0 |  | 0 | 0
PRE-CNG (032) | 6"& 8" Richland H.P. Line | 250 | 3 |  | 794 | 330 | 220 | NA |  | 220 |  | NA | UNVALID | 8.625 | 0.718 | 35000 | 0.8 | NO | NA | NA | 12.59% | NA | 1960 | 6592.2 | 83.59 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 6592.2 | 0 |  | 0 | 0
4500110 | HPSS 4500110 | 200 | 3 |  | 1549 | 112 | 74 | NA |  | 74 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1962 | 39.1 | 51.37 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 39.1 | 0 |  | 0 | 0
4790147 | HPSS 4790147 | 300 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1963 | 6 | 61.31 | Addressed w/ 116 Segment | 2021 | 1 | 0 | 6 | 0 |  | 0 | 0
4800080 | Inlet M&R 38509 | 150 | 3 |  | 499 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 9.01% | NA | 1966 | 49 | 76.51 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 49 | 0 |  | 0 | 0
11097 (1) | 4” Northwest Pasco H.P. Line | 300 | 3 |  | 877 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 10.26% | 8.14% | 1966 | 2881.7 | 91.76 | 116 Segment, Pressure Test | 2018 | 1 | 0 | 2881.7 | 0 |  | 0 | 0
12301 | 2" Burbank H.P. Line | 158 | 3 |  | 1361 | 100 | 71 | NA |  | 71 |  | NA | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.48% | 3.48% | 1967 | 3266.7 | 49.48 | 116 Segment, Pressure Test | 2017 | 1 | 0 | 3266.7 | 0 |  | 0 | 0
12614 | 4" East Finley H.P. Line | 250 | 3 |  | 877 | 120 | 85 | 250 |  | 85 |  | NA | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.78% | 1967 | 2504.9 | 67.55 | 116 Segment, Pressure Test | 2021 | 1 | 0 | 2504.9 | 0 |  | 0 | 0
13340 | Inlet 023-R-014 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 1967 | 10.8 | 88.02 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 10.8 | 0 |  | 0 | 0
4500106 | Inlet 023-R-016 | 250 | 3 |  | 933 | 750 | 535 | NA |  | 535 | X | Service | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NO | YES | 8.03% | 6.78% | 1967 | 5 | 54.53 | Accept Most Stringent Criteria | -- | 1 | 0 | 5 | 0 | 1 | 5 | 0 | 1
4500115 | HPSS 4500115 | 200 | 3 |  | 1549 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1967 | 46 | 45.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 46 | 0 |  | 0 | 0
14375 | 8"Attalia Transmission Line | 300 | 3 |  | 549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 12.75 | 0.25 | 35000 | 0.8 | YES | YES | YES | 21.86% | 21.86% | 1968 | 413.9 | 107.36 | 116 Segment, Replace | 2021 | 1 | 0 | 413.9 | 0 |  | 0 | 0
15029 | 4" Finley H.P. Line | 200 | 3 |  | 499 | 307 | 219 | 250 |  | 219 | X | NA | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 6.84% | 12.02% | 1968 | 2386.8 | 71.52 | Accept Most Stringent Criteria | -- | 1 | 0 | 2386.8 | 0 | 1 | 2386.8 | 0 | 1
15073 | Main Stub | 300 | 3 |  | 2123 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 4.24% | NA | 1968 | 11.5 | 41.74 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 11.5 | 0 |  | 0 | 0
15604 | 023-O-001 | 200 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 12.02% | NA | 1968 | 21.3 | 84.02 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 21.3 | 0 |  | 0 | 0
4500103 | HPSS 4500103 | 200 | 3 |  | 1549 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1968 | 14 | 44.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 14 | 0 |  | 0 | 0
4500104 | HPSS 4500104 | 200 | 3 |  | 1549 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1968 | 39 | 44.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 39 | 0 |  | 0 | 0
4500118 | HPSS 4500118 | 200 | 3 |  | 1549 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1968 | 37 | 44.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 37 | 0 |  | 0 | 0
4500130 | HPSS 4500130 | 200 | 3 |  | 1549 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1968 | 47.7 | 44.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 47.7 | 0 |  | 0 | 0
4500200 | Inlet M&R 15281 | 200 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1968 | 14 | 54.37 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 14 | 0 |  | 0 | 0
4790146 | HPSS 6856710936 | 300 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1968 | 60 | 56.31 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 60 | 0 |  | 0 | 0
16064 | 2" Main (Maple St) | 300 | 3 |  | 933 | 100 | 71 | 1440 |  | 71 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 9.64% | 1969 | 416.6 | 60.14 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 416.6 | 0 |  | 0 | 0
16255 | 4" East Finley H.P. Line | 250 | 3 |  | 877 | 703 | 502 | 275 |  | 275 | X | NA | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 8.55% | NA | 1969 | 1785 | 56.55 | Accept Most Stringent Criteria | -- | 1 | 0 | 1785 | 0 | 1 | 1785 | 0 | 1
16256 | Inlet 023-R-017 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 15.02% | 1969 | 365.2 | 87.02 | 116 Segment, Replace | 2021 | 1 | 0 | 365.2 | 0 |  | 0 | 0
4500109 | HPSS 4500109 | 250 | 3 |  | 1549 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1969 | 5 | 44.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 5 | 0 |  | 0 | 0
4790180 | Service Stub | 300 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1969 | 53 | 55.31 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 53 | 0 |  | 0 | 0
15798 | 4" Dodd Road H.P. Line | 300 | 3 |  | 877 | 700 | 500 | 1440 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 10.26% | 8.14% | 1970 | 3251.9 | 63.76 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 0 | 3251.9 | 0 |  | 0 | 0
4500100 | HPSS 4500100 | 200 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1971 | 17 | 40.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
4500112 | HPSS 4500112 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1975 | 62 | 46.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 62 |  | 0 | 0
25472 | Inlet 023-R-019 | 250 | 3 |  | 933 | 118 | 78 | 250 |  | 78 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1977 | 477.7 | 53.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 477.7 |  | 0 | 0
4741450 | HP Service Line (7131 N Railroad Ave) | 300 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1977 | 58 | 44.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
4800750 | HPSS 4800750 | 158 | 3 |  | 1193 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.97% | NA | 1977 | 20 | 37.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
52205 | Inlet 023-R-055 | 200 | 3 |  | 1361 | 700 | 466 | NA |  | 466 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 4.41% | 4.41% | 1978 | 111.7 | 34.91 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 111.7 |  | 0 | 0
4500122 | HPSS 4500122 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1978 | 5 | 37.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
26685 | 6"& 8" Richland H.P. Line | 250 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 16.38% | 15.02% | 1979 | 15020.1 | 74.38 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 15020.1 | 1 | 0 | 15020.1 |  | 1
4500119 | HPSS 4500119 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1979 | 16 | 36.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
2210 | Inlet 023-R-036 | 400 | 3 |  | 544 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 29.37% | NA | 1980 | 151.1 | 87.87 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 151.1 |  | 0 | 0
27994 | 4" Glade Road H.P. Line | 150 | 3 |  | 877 | 260 | 173 | NA |  | 173 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 5.13% | 4.07% | 1980 | 16.7 | 38.63 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 16.7 |  | 0 | 0
28141 | 4" Plymouth H.P. Line | 400 | 3 |  | 877 | 600 | 400 | NA |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 13.68% | 13.52% | 1980 | 3985.9 | 59.68 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3985.9 | 1 | 0 | 3985.9 |  | 1
28319 | Inlet 023-R-023 | 250 | 3 |  | 1361 | 105 | 70 | 1440 |  | 70 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1980 | 122.9 | 45.01 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 122.9 |  | 0 | 0
28546 | 6"& 8" Richland H.P. Line | 250 | 3 |  | 811 | 750 | 500 | NA |  | 500 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 12.32% | 9.57% | 1980 | 587.5 | 55.82 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 587.5 | 1 | 0 | 587.5 |  | 1
28040 | Inlet 023-R-025 | 300 | 3 |  | 1193 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 7.54% | 1981 | 28 | 49.54 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 28 |  | 0 | 0
28960 | 6"& 8" Richland H.P. Line | 250 | 3 |  | 802 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.188 | 46000 | 0.8 | NO | NO | YES | 12.47% | 11.55% | 1981 | 16799 | 65.47 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 16799 | 1 | 0 | 16799 |  | 1
29276 | 4" Paterson H.P. Line | 300 | 3 |  | 877 | 450 | 300 | 1440 |  | 300 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 1981 | 5904.4 | 62.26 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5904.4 | 1 | 0 | 5904.4 |  | 1
29291 | 8"Attalia Transmission Line | 300 | 3 |  | 811 | 450 | 300 | 720 |  | 300 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 14.79% | 11.48% | 1981 | 371.1 | 53.79 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 371.1 | 1 | 0 | 371.1 |  | 1
56710 | 4" Paterson H.P. Line | 300 | 3 |  | 877 | 450 | 300 | NA |  | 300 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 10.26% | 8.14% | 1981 | 1104.5 | 55.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1104.5 | 1 | 0 | 1104.5 |  | 1
4531195 | HPSS 4531195 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1981 | 86 | 36.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 86 |  | 0 | 0
4531210 | HPSS 4531210 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 58 | 36.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
30337 | Inlet 023-R-028 | 300 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 6.61% | 6.61% | 1983 | 25 | 38.61 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 25 |  | 0 | 0
31013 | 8"Attalia Transmission Line | 300 | 3 |  | 610 | 620 | 413 | 720 |  | 413 | X |  | UNVALID | 8.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 19.66% | 19.66% | 1983 | 416.7 | 57.66 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 416.7 |  | 0 | 0
59292 | Inlet 023-R-024 | 200 | 3 |  | 1361 | 375 | 250 | 1440 |  | 250 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 4.41% | NA | 1983 | 125.1 | 32.41 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 125.1 |  | 0 | 0
4500111 | HPSS 4500111 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.87% | 3.87% | 1983 | 53 | 34.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 53 |  | 0 | 0
4653008 | HPSS 4653008 | 400 | 3 |  | 933 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 12.85% | NA | 1983 | 25 | 53.85 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
31040 | Burbank H.P. Distribution System | 300 | 3 |  | 933 | 600 | 400 | NA |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 9.64% | 1984 | 84 | 45.14 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 84 | 1 | 0 | 84 |  | 1
31040 | Burbank H.P. Distribution System | 300 | 3 |  | 1193 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 7.54% | 1984 | 4518.6 | 50.54 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4518.6 | 1 | 0 | 4518.6 |  | 1
4742510 | Service Stub | 300 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1984 | 3.4 | 46.31 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 3.4 |  | 0 | 0
4790148 | HPSS 4790148 | 158 | 3 |  | 1549 | 225 | 150 | UNKV |  | 150 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.06% | 3.06% | 1985 | 142.2 | 35.06 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 142.2 |  | 0 | 0
4500114 | HPSS 4500114 | 200 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1986 | 126.1 | 35.37 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 126.1 |  | 0 | 0
4500113 | HPSS 4500113 | 200 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1987 | 154 | 33.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 154 |  | 0 | 0
4840780 | HPSS 4840780 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 6 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
35680 | Inlet 023-R-031 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1988 | 65.9 | 35.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 65.9 |  | 0 | 0
35771 | 8"Attalia Transmission Line | 300 | 3 |  | 610 | 780 | 520 | 720 |  | 520 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 19.66% | 19.66% | 1988 | 3196.7 | 65.66 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3196.7 | 1 | 0 | 3196.7 |  | 1
35509 | Inlet 023-R-030 | 300 | 3 |  | 1361 | 450 | 300 | 1440 |  | 300 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 6.61% | 6.61% | 1989 | 23.5 | 35.61 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 23.5 |  | 0 | 0
4500121 | HPSS 4500121 | 200 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1989 | 4 | 31.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4 |  | 0 | 0
4531200 | HPSS 4531200 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 103.8 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 103.8 |  | 0 | 0
4531225 | HPSS 4531225 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 23.5 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.5 |  | 0 | 0
4550625 | HPSS 4550625 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 65.8 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 65.8 |  | 0 | 0
39828 | 8"Attalia Transmission Line | 300 | 3 |  | 610 | 460 | 306 | 720 |  | 306 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 19.66% | 11.48% | 1990 | 1984.6 | 60.66 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1984.6 | 1 | 0 | 1984.6 |  | 1
4550612 | HPSS 4550610 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 112.1 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 112.1 |  | 0 | 0
38244 | 2" West Finley H.P. Line | 200 | 3 |  | 499 | 375 | 250 | 1440 |  | 250 | X | X | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 12.02% | 6.43% | 1991 | 2434 | 56.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2434 | 1 | 0 | 2434 |  | 1
4500101 | HPSS 4500101 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1991 | 19 | 30.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
4500225 | Service Stub | 200 | 3 |  | 1549 | 380 | 253 | 1440 |  | 253 | X | Service | VALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1991 | 7 | 30.87 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7 | 1 | 0 | 7 |  | 1
4550633 | HPSS 4550633 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 100.1 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 100.1 |  | 0 | 0
4650393 | HPSS 4650393 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 93 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 93 |  | 0 | 0
4654022 | HPSS 4654022 | 300 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1991 | 83 | 37.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 83 |  | 0 | 0
42282 | 4" Finley H.P. Line | 200 | 3 |  | 1193 | 500 | 333 | 1440 |  | 333 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 4.41% | 5.03% | 1992 | 392.9 | 37.53 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 392.9 |  | 0 | 0
42537 | Inlet 023-R-037 | 300 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 1992 | 25.1 | 34.11 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25.1 | 1 | 0 | 25.1 |  | 1
42763 | Inlet 023-R-038 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1992 | 105.1 | 34.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 105.1 | 1 | 0 | 105.1 |  | 1
4500123 | HPSS 4500123 | 200 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1992 | 123.1 | 31.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 123.1 |  | 0 | 0
4500125 | HPSS 4500125 | 200 | 3 |  | 1549 | 520 | 346 | UNKV |  | 346 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1992 | 85 | 30.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 85 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year | [5 empty] | 0 | 0
4500126 | HPSS 4500126 | 200 | 3 |  | 1549 | 550 | 366 | UNKV |  | 366 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.87% | 3.87% | 1992 | 54.7 | 30.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54.7 |  | 0 | 0
4650730 | HPSS 4650730 | 250 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 4.84% | 1992 | 287.8 | 40.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 287.8 |  | 0 | 0
4790136 | HPSS 4790136 | 300 | 3 |  | 1549 | 730 | 486 | UNKV |  | 486 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 5.81% | 5.81% | 1992 | 103 | 38.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 103 |  | 0 | 0
39724 | 023-R-015, 023-O-003 | 250 | 3 |  | 794 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 12.59% | 8.45% | 1993 | 193.6 | 45.59 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 193.6 |  | 0 | 0
45267 | Pasco H.P. Distribution System | 300 | 3 |  | 877 | 632 | 421 | 720 |  | 421 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 1993 | 225 | 47.26 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 225 |  | 0 | 0
45595 | Inlet 023-R-039 | 250 | 3 |  | 1193 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 6.28% | 1993 | 52.3 | 37.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 52.3 | 1 | 0 | 52.3 |  | 1
4500092 | HPSS 4500092 | 200 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1993 | 10 | 29.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
4531193 | HPSS 4531193 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 47 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
4531198 | HPSS 4531198 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 121.6 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 121.6 |  | 0 | 0
4550503 | HPSS 4550503 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1993 | 90 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 90 |  | 0 | 0
4550608 | HPSS 4550609 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 151 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 151 |  | 0 | 0
4790175 | HPSS 4790175 | 300 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 5.81% | 5.81% | 1993 | 52 | 36.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
46649 | 023-V-032 | 250 | 3 |  | NA | NA | NA | 1440 |  | 1440 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1994 | 0 | 21.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
47184 | Inlet 023-R-056 | 300 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 1994 | 77 | 33.11 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 77 | 1 | 0 | 77 |  | 1
4500097 | HPSS 4500097 | 200 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1994 | 36 | 29.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
4500134 | HPSS 4500134 | 200 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1994 | 9.9 | 29.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9.9 |  | 0 | 0
4550506 | HPSS 4550506 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1994 | 186.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 186.1 |  | 0 | 0
4554055 | HPSS 4554055 | 250 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1994 | 140.5 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 140.5 |  | 0 | 0
4554065 | HPSS 4554065 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 149.1 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 149.1 |  | 0 | 0
46898 | 4" North Pasco H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.78% | 1995 | 16199.7 | 53.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 16199.7 | 1 | 0 | 16199.7 |  | 1
48294 | 4" North Pasco H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1995 | 126.1 | 32.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 126.1 |  | 0 | 0
48401 | Pasco H.P. Distribution System | 300 | 3 |  | 877 | 650 | 433 | 720 |  | 433 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 1995 | 756.2 | 50.26 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 756.2 |  | 0 | 0
48918 | 4" East Port of Pasco H.P. Line | 300 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 18.03% | 1995 | 2125.7 | 60.53 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 2125.7 |  | 0 | 0
49723 | 4" North Pasco H.P. Line | 250 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1995 | 97.2 | 31.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 97.2 | 1 | 0 | 97.2 |  | 1
60042 | 4" North Pasco H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1995 | 120.1 | 32.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 120.1 |  | 0 | 0
4500098 | HPSS 4500098 | 200 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.87% | 3.87% | 1995 | 165 | 29.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 165 |  | 0 | 0
4500129 | Service Stub | 200 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1995 | 51 | 28.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
4554138 | HPSS 4554138 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 112.1 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 112.1 |  | 0 | 0
4694000 | HPSS 4694000 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 130 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 130 |  | 0 | 0
4800755 | HPSS 4800755 | 158 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.06% | NA | 1995 | 196 | 29.06 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 196 |  | 0 | 0
49759 | Inlet 023-R-050 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1996 | 103.1 | 32.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 103.1 |  | 0 | 0
50258 | 8" Attalia Transmission Line | 250 | 3 |  | 610 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 16.38% | 9.57% | 1996 | 214.4 | 47.88 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 214.4 | 1 | 0 | 214.4 |  | 1
51874 | 023-V-048 | 300 | 3 |  | 1045 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.322 | 35000 | 0.8 | NO | NO | YES | 11.48% | 11.48% | 1996 | 10.1 | 41.98 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 10.1 | 1 | 0 | 10.1 |  | 1
51874 | 023-V-048 | 300 | 3 |  | 1045 | 600 | 400 | UNKV |  | 400 | X | X | UNVALID | 8.625 | 0.322 | 35000 | 0.8 | YES | YES | YES | 11.48% | 11.48% | 1996 | 5 | 45.98 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
51880 | M&R 51880 | 300 | 3 |  | 544 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 22.02% | 22.02% | 1996 | 199.1 | 87.52 | Addressed w/ 116 Segment | 2021 | 1 | 1 | 0 | 199.1 |  | 0 | 0
52321 | 023-V-049 | 300 | 3 |  | 1056 | 600 | 400 | 720 |  | 400 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 11.36% | 10.14% | 1996 | 3.7 | 41.86 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3.7 | 1 | 0 | 3.7 |  | 1
52321 | 023-V-049 | 300 | 3 |  | 1056 | 600 | 400 | 720 |  | 400 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 11.36% | 10.14% | 1996 | 10 | 41.86 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 10 | 1 | 0 | 10 |  | 1
4500132 | HPSS 4500132 | 200 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1996 | 366.9 | 29.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 366.9 |  | 0 | 0
4736522 | HPSS 4736522 | 300 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1996 | 172 | 41.31 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 172 |  | 0 | 0
4736527 | HPSS 4736527 | 300 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1996 | 165.6 | 36.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 165.6 |  | 0 | 0
1540 | Service Stub (Boise Cascade) | 300 | 3 |  | 499 | 600 | 400 | NA |  | 400 | X | Service | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 18.03% | 18.03% | 1997 | 24 | 52.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 24 | 1 | 0 | 24 |  | 1
49482 | Inlet 023-R-040 | 300 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 6.61% | 6.61% | 1997 | 37 | 31.61 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 37 | 1 | 0 | 37 |  | 1
51334 | 4" North Pasco H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1997 | 476.1 | 34.55 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 476.1 |  | 0 | 0
51615 | 4" North Pasco H.P. Line | 250 | 3 |  | 1193 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 6.28% | 1997 | 160.8 | 36.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 160.8 | 1 | 0 | 160.8 |  | 1
52153 | Inlet 023-R-056 | 300 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 9.64% | NA | 1997 | 5 | 58.64 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 5 |  | 0 | 0
52176 | 4" East Port of Pasco H.P. Line | 300 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 1997 | 667.7 | 49.26 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 667.7 | 1 | 0 | 667.7 |  | 1
52386 | 8"Attalia Transmission Line | 300 | 3 |  | 499 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 18.03% | 1997 | 1387.5 | 59.53 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1387.5 |  | 0 | 0
53236 | 6"& 8" North Richland H.P. Line | 250 | 3 |  | 811 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 12.32% | 9.57% | 1997 | 18955.9 | 61.32 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 18955.9 | 1 | 0 | 18955.9 |  | 1
53238 | 6"& 8" North Richland H.P. Line | 250 | 3 |  | 794 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | NO | YES | 12.59% | 9.57% | 1997 | 23872.6 | 57.59 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23872.6 |  | 0 | 0
53587 | Inlet 023-R-061 | 250 | 3 |  | 933 | 750 | 500 | 300 |  | 300 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1997 | 9.7 | 37.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 9.7 | 1 | 0 | 9.7 |  | 1
4801377 | HPSS 4801377 | 300 | 3 |  | 933 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 9.64% | NA | 1997 | 95.1 | 38.64 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 95.1 |  | 0 | 0
2097 | Inlet 023-R-060 | 300 | 3 |  | 499 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 18.03% | 18.03% | 1998 | 74 | 56.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 74 |  | 0 | 0
53782 | 4" East Port of Pasco H.P. Line | 300 | 3 |  | 877 | 760 | 506 | 720 |  | 506 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 1998 | 4047.4 | 51.26 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 4047.4 |  | 0 | 0
54526 | Inlet 023-R-064 | 250 | 3 |  | 933 | 90 | 60 | 1440 |  | 60 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 1998 | 38 | 41.53 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
54648 | Inlet 023-R-065 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1998 | 70 | 30.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 70 |  | 0 | 0
54921 | 8"Attalia Transmission Line | 300 | 3 |  | 1045 | 450 | 300 | 720 |  | 300 | X | X | VALID | 8.625 | 0.25 | 46000 | 0.8 | NO | NO | YES | 11.25% | 11.48% | 1998 | 72 | 40.98 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 72 | 1 | 0 | 72 |  | 1
55746 | 4" North Pasco H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1998 | 83.5 | 30.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 83.5 |  | 0 | 0
55910 | Inlet 023-R-067 | 300 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 1998 | 29 | 31.11 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 29 |  | 0 | 0
56050 | 4" East Port of Pasco H.P. Line | 300 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 1998 | 764.9 | 48.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 764.9 | 1 | 0 | 764.9 |  | 1
4550603 | HPSS 4550603 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 32 | 29.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 32 |  | 0 | 0
4694005 | HPSS 4694005 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 8 | 29.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
4801379 | Inlet 023-R-068 | 300 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | Service | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 9.64% | 9.64% | 1998 | 18 | 38.14 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 18 | 1 | 0 | 18 |  | 1
2452610057 | HPSS 2452610057 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 30.1 | 38.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 30.1 |  | 0 | 0
1990 | Inlet 023-R-026 | 300 | 3 |  | 499 | 450 | 300 | UNKV |  | 300 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 18.03% | NA | 1999 | 23 | 51.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23 |  | 0 | 0
53627 | Inlet 023-R-059 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1999 | 20.4 | 29.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20.4 | 1 | 0 | 20.4 |  | 1
56711 | Inlet 023-R-069 | 300 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 1999 | 21 | 30.61 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21 | 1 | 0 | 21 |  | 1
4550596 | HPSS 4550596 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 31.8 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31.8 |  | 0 | 0
4553605 | HPSS 4553605 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 7 | 28.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
4553606 | HPSS 4553606 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 8 | 28.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
4692282 | HPSS 4692282 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 8 | 28.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
4694006 | HPSS 4694006 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 73 | 28.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 73 |  | 0 | 0
4790155 | HPSS 4790155 | 300 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 1999 | 9 | 33.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
4790167 | HPSS 4790104 | 300 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 5.81% | 5.81% | 1999 | 26 | 33.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26 |  | 0 | 0
38822 | 4" North Pasco H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2000 | 25 | 29.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 25 |  | 0 | 0
58329 | 023-V-075 | 200 | 3 |  | 877 | 400 | 266 | 275 |  | 266 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 6.84% | 5.42% | 2000 | 13 | 34.34 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 13 |  | 0 | 0
58505 | 4" North Pasco H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2000 | 14.5 | 29.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.5 |  | 0 | 0
59248 | Inlet 023-R-076 | 250 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 2000 | 97.9 | 35.53 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 97.9 |  | 0 | 0
4654023 | HPSS 4654023 | 300 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 2000 | 2 | 33.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
4741137 | HPSS 4741137 | 300 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 2000 | 18 | 38.31 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 18 |  | 0 | 0
59734 | 4" East Port of Pasco H.P. Line | 300 | 3 |  | 877 | 650 | 433 | 720 |  | 433 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 2001 | 689.4 | 47.26 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 689.4 |  | 0 | 0
59736 | Inlet 023-R-078 | 300 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 2001 | 126.1 | 30.61 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 126.1 |  | 0 | 0
59886 | Inlet 023-R-077 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2001 | 18 | 28.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 18 |  | 0 | 0
4554026 | HPSS 4554026 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2001 | 8 | 27.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
4950350 | HPSS 4950350 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2001 | 19 | 27.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
4554001 | HPSS 4554001 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 106.1 | 28.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 106.1 |  | 0 | 0
4555421 | HPSS 4555421 | 250 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 87 | 27.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 87 |  | 0 | 0
4694011 | HPSS 4694011 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 72 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 72 |  | 0 | 0
4801382 | HPSS 4801382 | 300 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 5.81% | NA | 2002 | 6 | 32.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
D0066671 | 6"& 8" Richland H.P. Line | 250 | 3 |  | 811 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 12.32% | 9.57% | 2002 | 14.5 | 43.82 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.5 |  | 0 | 0
D0067264 | Inlet 023-R-083 | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.78% | 2002 | 101.6 | 36.05 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 101.6 |  | 0 | 0
D0067948 | 4" East Port of Pasco H.P. Line | 300 | 3 |  | 877 | 650 | 433 | 720 |  | 433 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 8.14% | 2002 | 1035.6 | 49.26 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1035.6 |  | 0 | 0
D0068519 | Inlet 023-R-080 | 250 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2002 | 25 | 28.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 25 |  | 0 | 0
D0069144 | 4” Plymouth H.P. Line | 400 | 3 |  | 877 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 13.68% | NA | 2003 | 183.9 | 41.68 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 183.9 |  | 0 | 0
D0069531 | Inlet 023-R-082 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2003 | 69 | 27.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 69 | 1 | 0 | 69 |  | 1
D0070621 | Inlet 023-R-084 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2003 | 21 | 27.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21 | 1 | 0 | 21 |  | 1
D0070667 | 6" West Richland H.P. Line | 250 | 3 |  | 544 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 6.625 | 0.188 | 46000 | 0.8 | NO | YES | YES | 9.58% | 18.35% | 2003 | 2945.3 | 56.85 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 2945.3 |  | 0 | 0
D0071055 | Inlet 023-R-085 | 250 | 3 |  | 1052 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 7.12% | 8.45% | 2003 | 19.9 | 54.45 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 19.9 |  | 0 | 0
4500155 | HPSS 4500155 | 200 | 3 |  | 1549 | 750 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 2004 | 29 | 25.37 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 29 |  | 0 | 0
4682320 | HPSS 4682320 | 250 | 3 |  | 1549 | 650 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2004 | 9.5 | 26.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 9.5 |  | 0 | 0
4692278 | HPSS 4682275 | 250 | 3 |  | 1193 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2004 | 6 | 31.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
4696940 | HPSS 4696940 | 250 | 3 |  | 1549 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 12 | 26.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
4834860 | HPSS 4834860 | 250 | 3 |  | 1193 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2004 | 16 | 36.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
4835880 | HPSS 4835880 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2004 | 19 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
4950141 | HPSS 4950141 | 250 | 3 |  | 1549 | 750 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 12 | 26.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
4500137 | HPSS 4500137 | 200 | 3 |  | 1549 | 650 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 2005 | 9 | 24.87 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 9 |  | 0 | 0
4500138 | HPSS 4500138 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 2005 | 10 | 23.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
4554210 | HPSS 4554210 | 250 | 3 |  | 1549 | 700 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 22 | 25.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
D0075204 | Inlet 023-R-086 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2005 | 29 | 26.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 29 | 1 | 0 | 29 |  | 1
D0077942 | Inlet 023-R-087 | 250 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X | X | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NO | YES | 15.02% | 6.78% | 2005 | 42.3 | 45.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 42.3 | 1 | 0 | 42.3 |  | 1
D0078199 | Inlet 023-R-088 | 200 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NO | YES | 2.65% | 4.41% | 2005 | 47 | 20.41 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 47 |  | 0 | 0
D0078941 | 8" Attalia Transmission Line | 300 | 3 |  | 802 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 8.625 | 0.188 | 46000 | 0.8 | NO | NA | NA | 14.96% | NA | 2005 | 4430.7 | 48.46 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4430.7 | 1 | 0 | 4430.7 |  | 1
4692331 | HPSS 4692331 | 250 | 3 |  | 1549 | 450 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 9 | 25.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
4693504 | HPSS 4693504 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 18 | 24.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
4802500 | HPSS 4802500 | 300 | 3 |  | 2112 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.154 | 24000 | 0.6 | YES | NA | NA | 4.26% | NA | 2006 | 4 | 23.76 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4 |  | 0 | 0
D0078546 | Inlet 023-R-089 | 158 | 3 |  | 1361 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.48% | 3.48% | 2006 | 17 | 28.98 | Addressed w/ 116 Segment | 2017 | 1 | 1 | 0 | 17 |  | 0 | 0
D0080029 | Inlet 023-R-092 | 300 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 9.64% | NA | 2006 | 25 | 34.14 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
D0080137 | 2" Dietrich Rd H.P. Line | 300 | 3 |  | 933 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 9.64% | 2006 | 2318.1 | 41.64 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 2318.1 |  | 0 | 0
D0080697 | Inlet 023-R-093 | 300 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 9.64% | 2006 | 65 | 34.14 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 65 |  | 0 | 0
D0080711 | Inlet 023-R-089 | 158 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.48% | NA | 2006 | 48.1 | 19.98 | Addressed w/ 116 Segment | 2017 | 1 | 1 | 0 | 48.1 |  | 0 | 0
D0082224 | Inlet 023-R-109 | 250 | 3 |  | 2260 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 3.32% | NA | 2007 | 15 | 18.32 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 15 |  | 0 | 0
161298 | 4" Finley H.P. Line | 200 | 3 |  | 877 | 465 | 310 | NA |  | 310 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 6.84% | 5.42% | 2008 | 657 | 31.34 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 657 |  | 0 | 0
4500176 | Inlet M&R D0085404 | 200 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 12.02% | 12.02% | 2008 | 1581.6 | 68.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 1581.6 |  | 0 | 0
D0083934 | Inlet 023-R-096 | 250 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 7.12% | 15.02% | 2008 | 50.5 | 43.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 50.5 | 1 | 0 | 50.5 |  | 1
D0084203 | Inlet 023-R-097 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2008 | 55.5 | 25.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 55.5 | 1 | 0 | 55.5 |  | 1
D0084967 | Inlet 023-R-099 | 250 | 3 |  | 877 | 850 | 566 | UNKV |  | 566 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | NO | YES | 8.55% | 8.45% | 2008 | 774.4 | 33.05 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 774.4 |  | 0 | 0
161237 | Inlet 023-R-101 | 300 | 3 |  | 1361 | 600 | 400 | 740 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 2009 | 24.9 | 25.61 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 24.9 |  | 0 | 0
161240 | Inlet 023-R-098 | 300 | 3 |  | 499 | 95 | 63 | 1440 |  | 63 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 10.26% | 18.03% | 2009 | 43 | 51.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 43 |  | 0 | 0
163136 | Inlet 023-R-108 | 250 | 3 |  | 1193 | 500 | 333 | 720 |  | 333 | X | X | VALID | 1.05 | 0.113 | 35000 | 0.6 | NO | YES | YES | 3.32% | 6.28% | 2009 | 7.9 | 29.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7.9 | 1 | 0 | 7.9 |  | 1
163646 | Inlet 023-R-095 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 2009 | 25 | 51.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 25 |  | 0 | 0
166068 | Inlet 023-R-102 | 250 | 3 |  | 933 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 2009 | 71.4 | 51.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 71.4 |  | 0 | 0
D0085196 | Inlet 023-R-098 | 300 | 3 |  | NA | NA | NA | 720 |  | 720 | X |  | UNVALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2009 | 0 | 14 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
171773 | 6" West Richland H.P. Line | 250 | 3 |  | 544 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | YES | YES | 6.37% | 18.35% | 2010 | 2929.9 | 53.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2929.9 | 1 | 0 | 2929.9 |  | 1
4740096 | Inlet 023-R-103 | 300 | 3 |  | 1193 | 0 | 0 | 740 |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | YES | YES | 7.54% | 7.54% | 2010 | 16 | 50.04 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 16 |  | 0 | 0
177457 | Inlet 023-R-111 | 250 | 3 |  | 1303 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 52000 | 0.6 | NO | NO | YES | 5.75% | 4.56% | 2011 | 58.7 | 23.75 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 58.7 | 1 | 0 | 58.7 |  | 1
180655 | Inlet 023-R-112 | 250 | 3 |  | 1193 | 800 | 533 | 720 |  | 533 | X | X | VALID | 1.315 | 0.133 | 30000 | 0.6 | NO | YES | YES | 4.12% | 6.28% | 2011 | 20 | 28.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20 | 1 | 0 | 20 |  | 1
183235 | 4" Finley H.P. Line | 200 | 3 |  | 1052 | 860 | 573 | 720 |  | 573 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 5.70% | 5.42% | 2011 | 161.2 | 24.7 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 161.2 | 1 | 0 | 161.2 |  | 1
183768 | 8"Attalia Transmission Line | 300 | 3 |  | 1205 | 800 | 533 | 720 |  | 533 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 9.95% | 7.73% | 2011 | 770.5 | 32.95 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 770.5 | 1 | 0 | 770.5 |  | 1
188022 | 023-V-134 | 250 | 3 |  | 499 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 52000 | 0.8 | NO | YES | YES | 8.47% | 15.02% | 2011 | 136.8 | 63.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 136.8 |  | 0 | 0
194428 | Main to HPSS 1287597377 | 300 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 10.26% | 8.14% | 2012 | 35.2 | 32.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35.2 | 1 | 0 | 35.2 |  | 1
194550 | Inlet 023-R-114 | 300 | 3 |  | 1052 | 750 | 500 | 720 |  | 500 | X | Service | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NA | NA | 8.55% | NA | 2012 | 29 | 26.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 29 | 1 | 0 | 29 |  | 1
2634142817 | HPSS 2634142817 | 300 | 3 |  | 1193 | 100 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 7.54% | NA | 2012 | 15 | 34.04 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
3420329860 | HPSS 3420329860 | 300 | 3 |  | 933 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 9.64% | NA | 2012 | 77 | 31.14 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77 |  | 0 | 0
3894673266 | HPSS 3894673266 | 300 | 3 |  | 1193 | 850 | 566 | UNKV |  | 566 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 7.54% | NA | 2012 | 55 | 29.04 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
4898318305 | HPSS 4898318305 | 250 | 3 |  | 1549 | 100 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2012 | 9 | 22.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
194009 | Inlet 023-R-115 | 300 | 3 |  | 933 | 600 | 400 | 720 |  | 400 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 9.64% | 9.64% | 2013 | 25 | 30.64 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
200560 | 8"Attalia Transmission Line | 300 | 3 |  | 1205 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 9.95% | 7.73% | 2013 | 99.8 | 26.95 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 99.8 | 1 | 0 | 99.8 |  | 1
2076066725 | HPSS 2076066725 | 250 | 3 |  | 499 | 800 | 533 | UNKV |  | 499 | X | Service | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 15.02% | NA | 2013 | 18 | 41.02 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
4969344952 | HPSS 4969344952 | 250 | 3 |  | 1193 | 740 | 493 | UNKV |  | 493 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2013 | 15 | 27.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
200521-IN | Inlet 023-R-116 | 809 | 3 |  | 1643 | 1425 | 950 | 1440 |  | 950 | X | X | VALID | 4.5 | 0.237 | 52000 | 0.6 | NO | NO | YES | 14.77% | 14.77% | 2013 | 0 | 36.77 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
208908 | 2" Dietrich Rd H.P. Line | 300 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 2.375 | 0.154 | 52000 | 0.6 | YES | YES | YES | 4.45% | 7.54% | 2014 | 4583.1 | 35.54 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4583.1 |  | 0 | 0
213428 | 8"Attalia Transmission Line | 300 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | YES | YES | 11.48% | 18.03% | 2014 | 35.2 | 43.53 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35.2 | 1 | 0 | 35.2 |  | 1
4650395 | HPSS 4650395 | 250 | 3 |  | 980 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.66 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.65% | NA | 2014 | 3 | 33.15 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 3 |  | 0 | 0
1287597377 | HPSS 1287597377 | 300 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 7.54% | NA | 2014 | 21 | 28.04 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
216023 | Pasco H.P. Distribution System (023-V-171) | 300 | 3 |  | 499 | 755 | 503 | 720 |  | 499 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 8.55% | 18.03% | 2015 | 27 | 43.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 27 | 1 | 0 | 27 |  | 1
219407 | 8"Attalia Transmission Line | 300 | 3 |  | 1045 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | YES | YES | 11.48% | 7.73% | 2015 | 37.6 | 36.48 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 37.6 | 1 | 0 | 37.6 |  | 1
225109 | Inlet 023-R-084 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2015 | 0 | 11 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
4500107 | HPSS 4500107 | 250 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2015 | 33 | 19.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 33 |  | 0 | 0
5252249967 | HPSS 5252249967 | 250 | 3 |  | 2088 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 42000 | 0.6 | YES | NA | NA | 3.59% | NA | 2015 | 12 | 14.59 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
9356616640 | HPSS 9356616640 | 250 | 3 |  | 2088 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.315 | 0.109 | 42000 | 0.6 | YES | NA | NA | 3.59% | NA | 2015 | 21.3 | 14.59 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21.3 |  | 0 | 0
216023-T | 8"Attalia Transmission Line | 300 | 3 |  | 906 | 755 | 503 | 720 |  | 503 | X | X | VALID | 8.625 | 0.188 | 52000 | 0.8 | NO | NO | YES | 13.23% | 7.73% | 2015 | 0 | 34.23 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
KennL4-1 | Pasco H.P. Distribution System | 300 | 3 |  | 499 | 450 | 321 | 1440 |  | 321 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 18.03% | 8.14% | 2015 | 10721.7 | 58.03 | 116 Segment, Most Stringent Criteria | 2016 | 1 | 1 | 0 | 10721.7 |  | 0 | 0
11097 (2) | 4" Glade Road H.P. Line | 150 | 3 |  | 877 | 0 | 0 | 250 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.13% | 4.07% | 1966 | 2002.9 | 80.13 | 116 Segment, Pressure Test | 2018 | 1 | 0 | 2002.9 | 0 |  | 0 | 0
4950126 | Inlet M&R 53237 | 250 | 3 |  | 681 | 750 | 500 | NA |  | 500 | X | Service | VALID | 6.625 | 0.188 | 24000 | 1 | NO | YES | NO | 18.35% | 18.35% | 1997 | 27 | 50.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 27 | 1 | 0 | 27 |  | 1
DD000273 | Inlet 023-R-079 | 250 | 3 |  | 1843 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 1 | NO | NO | NO | 6.78% | 6.78% | 2001 | 116.1 | 48.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 116.1 |  | 0 | 0
194010 | Outlet 023-R-115 | 158 | 3 |  | 1361 | 375 | 250 | 720 |  | 250 | X | X | VALID | 2.375 | 0.154 | 42000 | 0.6 | NO | NO | YES | 2.90% | 3.48% | 2013 | 47.3 | 15.48 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 47.3 | 1 | 0 | 47.3 |  | 1
200521-OUT | Outlet 023-R-116 | 300 | 3 |  | 1643 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.237 | 52000 | 0.6 | NO | NO | YES | 5.48% | 5.48% | 2013 | 0 | 22.48 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year | [5 empty] | 0 | 0
6856710936 | HPSS 6856710936 | 300 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 5.81% | NA | 2014 | 2 | 46.31 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
189413 | Inlet 023-R-113 | 150 | 3 |  | 2738 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 52000 | 1 | NO | NO | NO | 2.74% | 2.74% | 2015 | 21 | 21.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
214539 (R-117 IN) | Inlet 023-R-117 | 811 | 3 |  | 2426 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.322 | 65000 | 1 | NO | NA | NA | 16.71% | NA | 2016 | 0 | 55.21 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 0 |  | 0 | 0
214539 (R-117 OUT) | Outlet 023-R-117 | 500 | 3 |  | 1507 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.25 | 52000 | 1 | NO | NA | NA | 16.59% | NA | 2016 | 0 | 55.09 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 0 |  | 0 | 0
214539 (R-120) | Inlet 023-R-120 | 500 | 3 |  | 1754 | 750 | 500 | 740 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 42000 | 1 | NO | NO | NO | 14.25% | 9.13% | 2016 | 43.6 | 32.75 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 43.6 |  | 0 | 0
9978315734 | HPSS 9978315734 | 300 | 3 |  | 3539 | 800 | 533 | 740 |  | 533 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NA | NA | 4.24% | NA | 2017 | 8 | 12.24 | No Action Needed | -- | 1 | 1 | 0 | 8 | 1 | 0 | 8 |  | 1
155676464 | HPSS 0155676464 | 200 | 3 |  | 3539 | 800 | 533 | 1440 |  | 533 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NA | NA | 2.82% | NA | 2017 | 14 | 10.82 | No Action Needed | -- | 1 | 1 | 0 | 14 | 1 | 0 | 14 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
Pre-CNGC-L1-1 | Longview-Kelso H.P. Distribution Line | 250 | 4 |  | 301 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 12.75 | 0.25 | 24000 | 0.8 | NO | NA | NA | 26.56% | NA | 1957 | 20341 | 169.06 | 116 Segment, Replace | 2017-2021 | 1 | 0 | 20341 | 0 |  | 0 | 0
Pre-CNGC-L1-1 | Longview-Kelso H.P. Distribution Line | 250 | 4 |  | 301 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 12.75 | 0.25 | 24000 | 0.8 | NO | YES | YES | 26.56% | 26.56% | 1957 | 4421.8 | 161.56 | 116 Segment, Replace | 2017-2021 | 1 | 0 | 4421.8 | 0 |  | 0 | 0
PRE-CNG (011-R-001) | Inlet 011-R-001 | 250 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 23.89% | 23.89% | 1956 | 9.1 | 120.39 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 9.1 | 0 |  | 0 | 0
Pre-CNGC-L1-2 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 1957 | 3108.6 | 105.52 | 116 Segment, Most Stringent Criteria | 2016 | 1 | 0 | 3108.6 | 0 |  | 0 | 0
28621 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 376 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 12.75 | 0.25 | 52000 | 0.8 | NO | YES | YES | 12.26% | 26.56% | 1980 | 988.7 | 104.06 | 116 Segment, Pressure Test | 2021 | 1 | 1 | 0 | 988.7 |  | 0 | 0
PRE-CNG (Inlet 011-R- | Inlet 011-R-020 | 250 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 23.89% | 23.89% | 1971 | 93.1 | 100.89 | Addressed w/ 116 Segment | 2017-2021 | 1 | 1 | 0 | 93.1 |  | 0 | 0
UNKV (Kalama) | 8" Kalama H.P. Line | 300 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 28.67% | NA | 1996 | 708.4 | 108.17 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 708.4 |  | 0 | 0
82C8335-3 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 24000 | 0.6 | NO | YES | YES | 12.47% | 15.02% | 1965 | 151.2 | 91.02 | 116 Segment, Replace | 2019 | 1 | 0 | 151.2 | 0 |  | 0 | 0
51820 | 8" Kalama Transmission Line | 300 | 3 |  | 418 | 750 | 500 | 720 |  | 418 | X | X | VALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 28.67% | 28.67% | 1996 | 7731.5 | 98.17 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7731.5 | 1 | 0 | 7731.5 |  | 1
52389 | 011-V-049 | 300 | 3 |  | 544 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 22.02% | NA | 1997 | 4.3 | 86.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 4.3 |  | 0 | 0
51820 | 8" Kalama H.P. Line | 300 | 3 |  | 418 | 750 | 500 | 720 |  | 418 | X | X | VALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 28.67% | 28.67% | 1996 | 1745.1 | 95.67 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1745.1 | 1 | 0 | 1745.1 |  | 1
PRE-CNG (Main Stub) | Main Stub | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1957 | 1 | 84.53 | Addressed w/ 116 Segment | 2017-2021 | 1 | 0 | 1 | 0 |  | 0 | 0
82C8335-2 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1965 | 516.2 | 81.53 | 116 Segment, Replace | 2019 | 1 | 0 | 516.2 | 0 |  | 0 | 0
PRE-CNG (Inlet 011-R- | Inlet 011-R-002 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 1972 | 41.8 | 81.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 41.8 |  | 0 | 0
14616 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 728 | 520 | UNKV |  | 499 | X | NA | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 8.55% | 15.02% | 1968 | 4176.5 | 74.52 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 4176.5 | 0 |  | 0 | 0
16460 | Inlet 011-R-050 | 300 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 9.64% | NA | 1969 | 20 | 74.14 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 20 | 0 |  | 0 | 0
52192 | Main Stub | 300 | 3 |  | 418 | 175 | 116 | NA |  | 116 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 28.67% | NA | 1997 | 0.1 | 82.67 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 0.1 |  | 0 | 0
24676 | 4" Kalama H.P. Line | 300 | 4 |  | 399 | 620 | 413 | NA |  | 399 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 18.03% | 18.03% | 1976 | 8071.8 | 74.53 | 116 Segment, Replace | 2021 | 1 | 1 | 0 | 8071.8 |  | 0 | 0
PRE-CNG (Inlet 011-R- | Inlet 011-R-003 | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 1970 | 33 | 71.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 33 | 0 |  | 0 | 0
15953 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 549 | 785 | 560 | NA |  | 549 | X | NA | VALID | 12.75 | 0.25 | 35000 | 0.8 | NO | NA | NA | 18.21% | NA | 1969 | 942.7 | 70.21 | Accept Most Stringent Criteria | -- | 1 | 0 | 942.7 | 0 | 1 | 942.7 | 0 | 1
25726 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 430 | 286 | NA |  | 286 | X | X | VALID | 12.75 | 0.25 | 35000 | 0.8 | NO | YES | YES | 18.21% | 18.21% | 1978 | 4322.7 | 69.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4322.7 | 1 | 0 | 4322.7 |  | 1
E0066903 | 011-O-002 | 250 | 3 |  | 564 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 12.75 | 0.25 | 52000 | 0.8 | NO | YES | YES | 12.26% | 17.71% | 2002 | 26.3 | 69.21 | Addressed w/ 116 Segment | 2017-2021 | 1 | 1 | 0 | 26.3 |  | 0 | 0
82C8335 | 4" Dike Road H.P. Line | 80 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 24000 | 0.6 | NO | YES | YES | 3.99% | 4.81% | 1965 | 6344.9 | 68.31 | 116 Segment, Replace | 2018 | 1 | 0 | 6344.9 | 0 |  | 0 | 0
23046 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 760 | 506 | NA |  | 499 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 1974 | 1350.4 | 68.02 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1350.4 |  | 0 | 0
43600 | 12" South Longview H.P. Line | 499 | 3 |  | 1017 | 1080 | 720 | 720 |  | 720 | X | X | VALID | 12.75 | 0.312 | 52000 | 0.8 | NO | YES | YES | 19.61% | 18.88% | 1995 | 22387.2 | 69.61 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 22387.2 | 1 | 0 | 22387.2 |  | 1
192344 | M&R 192344 | 250 | 3 |  | 544 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 18.35% | 18.35% | 2013 | 38.5 | 64.35 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 38.5 |  | 0 | 0
32764 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 549 | 455 | 303 | NA |  | 303 | X | X | VALID | 12.75 | 0.25 | 35000 | 0.8 | NO | NO | YES | 18.21% | 12.14% | 1985 | 1149.9 | 61.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1149.9 | 1 | 0 | 1149.9 |  | 1
52388 | 011-O-007 | 300 | 3 |  | 1056 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 11.36% | 10.14% | 1997 | 27 | 61.36 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 27 |  | 0 | 0
165133 | Inlet 011-R-046 | 499 | 3 |  | 877 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 17.06% | 13.54% | 2009 | 40 | 61.06 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 40 |  | 0 | 0
1661 | M&R 13913, 45514, E0083149 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 2013 | 4 | 61.02 | Addressed w/ 116 Segment | 2017-2021 | 1 | 1 | 0 | 4 |  | 0 | 0
35534 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 375 | 250 | NA |  | 250 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1988 | 1131 | 61.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1131 | 1 | 0 | 1131 |  | 1
21727 | Inlet 011-R-014 | 250 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1975 | 83.5 | 60.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 83.5 | 1 | 0 | 83.5 |  | 1
60516 | 8" Kalama Transmission Line | 300 | 3 |  | 716 | 790 | 526 | 720 |  | 526 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 14.79% | 16.74% | 2001 | 62.4 | 58.74 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 62.4 |  | 0 | 0
25725 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 549 | 440 | 293 | 960 |  | 293 | X | X | VALID | 12.75 | 0.25 | 35000 | 0.8 | NO | NO | YES | 18.21% | 12.14% | 1978 | 267.5 | 58.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 267.5 | 1 | 0 | 267.5 |  | 1
43601 | Outlet 011-R-030 | 250 | 3 |  | 564 | 375 | 250 | 960 |  | 250 | X | X | VALID | 12.75 | 0.312 | 35000 | 0.8 | NO | NO | YES | 17.71% | 12.14% | 1995 | 500.5 | 57.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 500.5 | 1 | 0 | 500.5 |  | 1
16087 | Inlet 011-R-018 | 250 | 3 |  | 933 | 110 | 78 | NA |  | 78 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1969 | 56.7 | 57.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 56.7 | 0 |  | 0 | 0
47136 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 600 | 400 | NA |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1994 | 744.7 | 55.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 744.7 | 1 | 0 | 744.7 |  | 1
E0073430 | Inlet 011-R-050 | 300 | 3 |  | 933 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 9.64% | 9.64% | 2004 | 2.5 | 55.14 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 2.5 |  | 0 | 0
E0084526 | Inlet 011-R-044 | 300 | 3 |  | 933 | 0 | 0 | 300 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 9.64% | 2008 | 129.3 | 54.14 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 129.3 |  | 0 | 0
49630 | Inlet 011-R-032 | 300 | 3 |  | 499 | 900 | 600 | 1440 |  | 499 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 6.61% | 18.03% | 1995 | 108.1 | 54.03 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 108.1 |  | 0 | 0
E0072366 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 18.35% | 15.02% | 2004 | 616.8 | 53.85 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 616.8 |  | 0 | 0
60516 | 8" Kalama Transmission Line | 300 | 3 |  | 811 | 790 | 526 | 720 |  | 526 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 14.79% | 11.48% | 2001 | 146.4 | 53.79 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 146.4 |  | 0 | 0
52189 | 011-V-042, 046 | 300 | 3 |  | 1106 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 46000 | 0.6 | NO | NO | YES | 6.19% | 8.14% | 1996 | 95.4 | 53.64 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 95.4 |  | 0 | 0
49627 | 6" Kalama H.P. Line | 300 | 3 |  | 794 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | YES | NO | YES | 15.10% | 10.14% | 1995 | 3597.4 | 53.6 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 3597.4 |  | 0 | 0
35461 | 011-V-019 | 250 | 3 |  | 499 | 375 | 250 | 400 |  | 250 | X | X | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 1988 | 30 | 53.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 30 | 1 | 0 | 30 |  | 1
PRE-CNG (Inlet 011-R- | Inlet 011-R-048 | 150 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 4.82% | 4.82% | 1970 | 5 | 53.32 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 5 | 0 |  | 0 | 0
3150200 | HPSS 3150200 | 300 | 3 |  | 499 | 900 | 600 | UNKV |  | 499 | X | Service | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 18.03% | NA | 1995 | 82.1 | 53.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 82.1 |  | 0 | 0
2742110 | HPSS 2742110 | 250 | 3 |  | 1214 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | NO | NA | NA | 6.18% | NA | 1972 | 60 | 52.68 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 60 |  | 0 | 0
43601 (011-V-031) | 011-V-031 | 499 | 3 |  | 1122 | 1080 | 720 | 720 |  | 720 | X | X | VALID | 12.75 | 0.344 | 52000 | 0.8 | NO | YES | YES | 17.78% | 16.31% | 1995 | 16 | 52.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 16 | 1 | 0 | 16 |  | 1
173404 | 011-O-005 | 150 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 42000 | 0.6 | NO | YES | YES | 3.39% | 9.01% | 2010 | 90.5 | 51.51 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 90.5 |  | 0 | 0
52844 | 8" Kalama H.P. Line | 300 | 3 |  | 1045 | 168 | 112 | NA |  | 112 |  | X | UNVALID | 8.625 | 0.25 | 46000 | 0.8 | NO | NO | YES | 11.25% | 11.48% | 1997 | 724.3 | 51.48 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 724.3 |  | 0 | 0
43606 | Inlet 011-R-030 | 499 | 3 |  | 1045 | 1080 | 720 | 720 |  | 720 | X | X | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NO | YES | 19.09% | 16.87% | 1995 | 115 | 51.09 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 115 | 1 | 0 | 115 |  | 1
887 | Inlet 011-R-031 | 250 | 3 |  | 499 | 660 | 440 | NA |  | 440 | X | Service | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 1994 | 7 | 50.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7 | 1 | 0 | 7 |  | 1
E0065695 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 685 | 740 | 493 | 960 |  | 493 | X |  | UNVALID | 12.75 | 0.312 | 35000 | 0.8 | NO | NO | YES | 14.59% | 12.14% | 2001 | 1193.1 | 50.09 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1193.1 |  | 0 | 0
43607 | M&R 43607 | 499 | 3 |  | 1045 | 1080 | 720 | NA |  | 720 | X | Service | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NO | YES | 19.09% | 16.87% | 1995 | 99 | 50.09 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 99 | 1 | 0 | 99 |  | 1
52438 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 499 | 600 | 400 | UNKV |  | 400 | X | X | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 8.55% | 15.02% | 1998 | 335.7 | 49.52 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 335.7 |  | 0 | 0
36627 | 4" Woodland H.P. Line | 150 | 3 |  | 499 | 460 | 306 | NA |  | 306 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.13% | 9.01% | 1989 | 2582.9 | 49.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2582.9 | 1 | 0 | 2582.9 |  | 1
EE001104 | Inlet 011-R-042 | 300 | 3 |  | 1106 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 8.14% | 8.14% | 2005 | 19.7 | 49.14 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 19.7 |  | 0 | 0
59671 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 685 | 720 | 480 | 400 |  | 400 | X | X | VALID | 12.75 | 0.312 | 35000 | 0.8 | NO | NO | YES | 14.59% | 12.14% | 2003 | 3546.5 | 49.09 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3546.5 | 1 | 0 | 3546.5 |  | 1
49628 | 6" Kalama H.P. Line | 300 | 3 |  | 877 | 900 | 600 | 720 |  | 600 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 10.26% | NA | 1995 | 1146.8 | 48.76 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1146.8 |  | 0 | 0
198862 | Longview-Kelso H.P. Distribution Line | 250 | 4 |  | 399 | 750 | 500 | 720 |  | 399 | X | X | VALID | 12.75 | 0.312 | 52000 | 0.8 | NO | YES | YES | 10.12% | 15.02% | 2013 | 3207 | 50.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3207 | 1 | 0 | 3207 |  | 1
2980300 | HPSS 2980300 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1965 | 36 | 48.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 36 | 0 |  | 0 | 0
165128 | 12" South Longview H.P. Line | 499 | 3 |  | 1223 | 1080 | 720 | 720 |  | 720 | X |  | UNVALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NO | YES | 16.31% | 16.31% | 2009 | 1326.1 | 47.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1326.1 |  | 0 | 0
23111 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1976 | 38 | 47.53 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 38 |  | 0 | 0
2980170 | HPSS 2980170 | 250 | 3 |  | 1549 | 30 | 21 | NA |  | 21 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1967 | 44 | 47.34 | Addressed w/ 116 Segment | 2017-2021 | 1 | 0 | 44 | 0 |  | 0 | 0
2980320 | HPSS 2980320 | 250 | 3 |  | 1549 | 30 | 21 | NA |  | 21 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1967 | 40 | 47.34 | Addressed w/ 116 Segment | 2017-2021 | 1 | 0 | 40 | 0 |  | 0 | 0
24703 | Inlet 011-R-024 | 300 | 3 |  | 1361 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 1977 | 23.4 | 46.61 | Addressed w/ 116 Segment | 2021 | 1 | 1 | 0 | 23.4 |  | 0 | 0
3130092 | HPSS 3130092 | 300 | 3 |  | 499 | 775 | 516 | UNKV |  | 499 | X | Service | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 18.03% | NA | 2008 | 15 | 46.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
49633 | Inlet 011-R-033 | 300 | 3 |  | 794 | 900 | 600 | 720 |  | 600 | X |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 15.10% | 10.14% | 1995 | 7 | 46.1 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 7 |  | 0 | 0
3130030 | HPSS 3130030 | 300 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 5.81% | 5.81% | 1976 | 49.1 | 45.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.1 |  | 0 | 0
2980280 | HPSS 2980280 | 250 | 3 |  | 1549 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1970 | 57.1 | 44.34 | Addressed w/ 116 Segment | 2017-2021 | 1 | 0 | 57.1 | 0 |  | 0 | 0
2742105 | HPSS 2742105 | 250 | 3 |  | 1193 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1979 | 63 | 44.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 63 |  | 0 | 0
E0084018 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 617 | 750 | 500 | 720 |  | 500 | X | X | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NO | YES | 8.17% | 12.14% | 2008 | 4297.8 | 44.14 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4297.8 | 1 | 0 | 4297.8 |  | 1
E0072303 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 815 | 600 | 400 | 960 |  | 400 | X | X | VALID | 12.75 | 0.25 | 52000 | 0.8 | NO | NO | YES | 12.26% | 12.14% | 2004 | 182.8 | 43.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 182.8 | 1 | 0 | 182.8 |  | 1
173058 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 815 | 812 | 541 | 400 |  | 400 | X | X | VALID | 12.75 | 0.25 | 52000 | 0.8 | NO | NO | YES | 12.26% | 8.17% | 2010 | 1551.4 | 43.26 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1551.4 | 1 | 0 | 1551.4 |  | 1
59951 | 8" Kalama H.P. Line | 300 | 3 |  | 811 | 810 | 540 | NA |  | 540 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NA | NA | 14.79% | NA | 2001 | 83.1 | 42.79 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 83.1 |  | 0 | 0
2980305 | Service Stub | 250 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NO | YES | 4.84% | 3.32% | 1991 | 2 | 41.84 | Addressed w/ 116 Segment | 2017-2021 | 1 | 1 | 0 | 2 |  | 0 | 0
E0082119 | 8" Kalama Transmission Line | 300 | 3 |  | 1045 | 730 | 486 | NA |  | 486 | X | X | VALID | 8.625 | 0.322 | 42000 | 0.8 | NO | NO | YES | 9.57% | 11.48% | 2007 | 646.9 | 41.48 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 646.9 | 1 | 0 | 646.9 |  | 1
E0072367 | 011-V-069, 070 | 250 | 3 |  | 811 | 410 | 273 | 720 |  | 273 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 12.32% | 12.14% | 2001 | 109 | 41.32 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 109 | 1 | 0 | 109 |  | 1
2742125 | HPSS 2742125 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1985 | 60.1 | 41.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60.1 |  | 0 | 0
13163 | 011-R-021, 011-O-001 | 152 | 3 |  | 1361 | 225 | 150 | NA |  | 150 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.35% | NA | 1968 | 7.9 | 40.85 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 7.9 | 0 |  | 0 | 0
2980295 | HPSS 2980295 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1973 | 40.6 | 40.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.6 |  | 0 | 0
2980307 | HPSS 2980307 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1973 | 11 | 40.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
2742054 | HPSS 2742054 | 250 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1995 | 4 | 39.84 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 4 |  | 0 | 0
2742100 | HPSS 2742100 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1978 | 113.6 | 39.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 113.6 |  | 0 | 0
166621 | 4" Woodland H.P. Line | 150 | 3 |  | 499 | 375 | 250 | NA |  | 250 | X | X | VALID | 4.5 | 0.188 | 24000 | 0.6 | NO | YES | YES | 7.48% | 9.01% | 2010 | 1691.1 | 39.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1691.1 | 1 | 0 | 1691.1 |  | 1
E0073431 | 6" South Kalama H.P. Line | 300 | 3 |  | 1044 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 6.625 | 0.188 | 46000 | 0.8 | YES | NO | YES | 11.49% | 10.14% | 2004 | 439.8 | 38.99 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 439.8 |  | 0 | 0
2910525 | HPSS 2910525 | 499 | 3 |  | 1549 | 1100 | 733 | UNKV |  | 733 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.66% | NA | 1997 | 34 | 38.66 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34 |  | 0 | 0
2910535 | HPSS 2910535 | 499 | 3 |  | 1549 | 1200 | 800 | UNKV |  | 800 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 9.66% | 9.66% | 1998 | 30.8 | 38.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30.8 |  | 0 | 0
2980314 | HPSS 2980314 | 250 | 3 |  | 1549 | 850 | 566 | UNKV |  | 566 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 7 | 36.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
177226 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 1082 | 840 | 560 | NA |  | 560 | X | X | VALID | 12.75 | 0.375 | 46000 | 0.8 | NO | NO | YES | 9.24% | 8.17% | 2012 | 7654 | 36.74 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7654 | 1 | 0 | 7654 |  | 1
EE000176 | Inlet 011-R-017 | 250 | 3 |  | 1549 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2002 | 4.7 | 36.34 | Addressed w/ 116 Segment | 2017-2021 | 1 | 1 | 0 | 4.7 |  | 0 | 0
2980200 | HPSS 2980200 | 250 | 3 |  | 1193 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1995 | 36 | 36.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
32982 | Inlet 011-R-011 | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1986 | 14.7 | 36.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.7 |  | 0 | 0
53094 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 1017 | 600 | 400 | 400 |  | 400 | X |  | UNVALID | 12.75 | 0.312 | 52000 | 0.8 | NO | NO | YES | 9.82% | 8.17% | 1997 | 108.3 | 35.82 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 108.3 |  | 0 | 0
2742051 | HPSS 2742051 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 29 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29 |  | 0 | 0
2980290 | HPSS 2980290 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1988 | 97.1 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 97.1 |  | 0 | 0
2980292 | HPSS 2980292 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1988 | 78.3 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 78.3 |  | 0 | 0
1317 | M&R E0082073 | 250 | 3 |  | 933 | 750 | 500 | NA |  | 500 | X | Service | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | YES | YES | 8.17% | 8.03% | 2007 | 230.1 | 33.17 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 230.1 | 1 | 0 | 230.1 |  | 1
1495 | HPSS 1495 | 250 | 3 |  | 933 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 2005 | 29.6 | 33.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29.6 |  | 0 | 0
192408 | 6" South Kalama H.P. Line | 300 | 3 |  | 1569 | 845 | 563 | NA |  | 563 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 7.64% | 6.83% | 2012 | 1860.2 | 32.64 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1860.2 | 1 | 0 | 1860.2 |  | 1
E0065803 | Inlet 011-R-038 | 250 | 3 |  | 877 | 700 | 466 | 720 |  | 466 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 2001 | 15 | 31.55 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 15 |  | 0 | 0
2930570 | HPSS 2930570 | 250 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1994 | 11 | 31.34 | Addressed w/ 116 Segment | 2017-2021 | 1 | 1 | 0 | 11 |  | 0 | 0
124 | HPSS 124 | 80 | 3 |  | 499 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 4.81% | NA | 1994 | 203.4 | 31.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 203.4 |  | 0 | 0
190874 | Inlet 011-R-008 | 250 | 3 |  | 1066 | 850 | 566 | 720 |  | 566 | X | X | VALID | 8.625 | 0.25 | 46000 | 0.8 | NO | YES | YES | 9.38% | 8.17% | 2012 | 46 | 30.88 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 46 | 1 | 0 | 46 |  | 1
2742052 | HPSS 2742052 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1994 | 65 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 65 |  | 0 | 0
2980316 | HPSS 2980316 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 30 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
2930817 | HPSS 2930817 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 2.6 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2.6 |  | 0 | 0
199748 | Inlet 011-R-050 | 300 | 3 |  | 1361 | 101.2 | 67 | 1440 |  | 67 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 6.61% | 6.61% | 2013 | 4.5 | 28.61 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 4.5 |  | 0 | 0
2742281 | HPSS 2742281 | 250 | 3 |  | 1549 | 650 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2005 | 33 | 25.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 33 |  | 0 | 0
189505 | Longview-Kelso H.P. Distribution Line | 250 | 3 |  | 1223 | 600 | 400 | 720 |  | 400 | X | X | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NA | NA | 8.17% | NA | 2012 | 25 | 25.67 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
197085 | Inlet 011-R-049 | 300 | 3 |  | 1361 | 845 | 563 | 720 |  | 563 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 6.61% | 6.83% | 2012 | 55.5 | 24.33 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 55.5 | 1 | 0 | 55.5 |  | 1
2980318 | HPSS 2980318 | 250 | 3 |  | 2260 | 950 | 633 | UNKV |  | 633 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 1999 | 54 | 22.32 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
2980275 | HPSS 2980275 | 250 | 3 |  | 2260 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2000 | 45 | 21.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
2660271 | HPSS 2660271 | 250 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 2012 | 77 | 21.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77 |  | 0 | 0
2770482 | HPSS 2770482 | 250 | 4 |  | 1808 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2001 | 17 | 23.32 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
9301367742 | HPSS 9301367742 | 250 | 3 |  | 1740 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.315 | 0.109 | 35000 | 0.6 | YES | NA | NA | 4.31% | NA | 2013 | 75 | 16.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 75 |  | 0 | 0
6521322387 | HPSS 6521322387 | 250 | 3 |  | 3766 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 1 | YES | NA | NA | 3.32% | NA | 2016 | 56 | 11.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
11C1144 | 8" March Point Transmission Line | 360 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 34.41% | 34.41% | 1957 | 144.4 | 155.91 | 116 Segment, Replace | 2018 | 1 | 0 | 144.4 | 0 |  | 0 | 0
1701 | 8" Anacortes Transmission Line | 360 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 34.41% | 34.41% | 1957 | 90671.6 | 199.91 | 116 Segment, Pressure Test/Replace | 2019 | 1 | 0 | 90671.6 | 0 |  | 0 | 0
11C1144 | 8" March Point Transmission Line | 360 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 34.41% | 34.41% | 1957 | 8641.6 | 174.91 | 116 Segment, Replace | 2018 | 1 | 0 | 8641.6 | 0 |  | 0 | 0
11C1144 | 8" March Point Transmission Line | 360 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 34.41% | 34.41% | 1957 | 144.4 | 155.91 | 116 Segment, Replace | 2018 | 1 | 0 | 144.4 | 0 |  | 0 | 0
11C5628 | 8" March Point Transmission Line | 360 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 34.41% | 34.41% | 1963 | 338.3 | 149.91 | 116 Segment, Replace | 2018 | 1 | 0 | 338.3 | 0 |  | 0 | 0
30636 | 16" Fredonia Transmission Line (M&R 30637) | 500 | 3 |  | 656 | 750 | 500 | NA |  | 500 | X | X | VALID | 16 | 0.28 | 52000 | 1 | NO | NO | YES | 27.47% | 30.48% | 1983 | 57.7 | 102.48 | No Action Needed | -- | 1 | 1 | 0 | 57.7 | 1 | 0 | 57.7 |  | 1
30636-T | 16" Fredonia Transmission Line | 500 | 3 |  | 737 | 750 | 500 | 720 |  | 500 | X | X | VALID | 16 | 0.281 | 52000 | 1 | NO | YES | YES | 30.48% | 27.11% | 1983 | 65218.3 | 116.48 | No Action Needed | -- | 1 | 1 | 0 | 65218.3 | 1 | 0 | 65218.3 |  | 1
40000 | 16" March Point Transmission Line | 500 | 3 |  | 913 | 750 | 500 | NA |  | 500 | X | X | VALID | 16 | 0.281 | 52000 | 1 | NO | NO | NO | 27.37% | 27.37% | 1992 | 43391.8 | 102.87 | No Action Needed | -- | 1 | 1 | 0 | 43391.8 | 1 | 0 | 43391.8 |  | 1
18191 | 8" Anacortes Transmission Line | 360 | 3 |  | 610 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 23.59% | 20.09% | 1972 | 236.4 | 121.09 | 116 Segment, Pressure Test | 2018 | 1 | 1 | 0 | 236.4 |  | 0 | 0
40021 | 16" March Point Transmission Line (017-V-050, 051, | 500 | 3 |  | 730 | 750 | 500 | 720 |  | 500 | X | X | VALID | 16 | 0.375 | 52000 | 0.8 | NO | YES | YES | 20.51% | 27.37% | 1992 | 53.3 | 83.87 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 53.3 | 1 | 0 | 53.3 |  | 1
17206 | 6" North Oak Harbor H.P. Line | 400 | 3 |  | 953 | 675 | 450 | 275 |  | 275 |  |  | UNVALID | 6.625 | 0.188 | 42000 | 1 | NO | NO | YES | 16.78% | 16.78% | 1972 | 18314 | 74.28 | 116 Segment, Expose/Verify | 2017 | 1 | 1 | 0 | 18314 |  | 0 | 0
MTVL4-1 | 4” Mount Vernon H.P. Line | 250 | 4 |  | 399 | 400 | 266 | NA |  | 266 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 2009 | 29629.7 | 60.02 | 116 Segment, Most Stringent Criteria | 2016 | 1 | 1 | 0 | 29629.7 |  | 0 | 0
Fish 18C4272 | 4" Arlington H.P. Line | 249 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 14.96% | 14.96% | 1961 | 10707.9 | 108.96 | 116 Segment, Replace | 2020 | 1 | 0 | 10707.9 | 0 |  | 0 | 0
211220 | 3" Burlington H.P. Line | 249 | 3 |  | 641 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 11.64% | NA | 1957 | 5385.7 | 104.64 | 116 Segment, Replace | 2017 | 1 | 0 | 5385.7 | 0 |  | 0 | 0
11C2775 | 4" North Texas Rd H.P. Line | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1960 | 917.9 | 86.53 | 116 Segment, Replace | 2021 | 1 | 0 | 917.9 | 0 |  | 0 | 0
11C1491 | Anacortes H.P. Distribution System | 105 | 3 |  | 544 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | NA | NA | 7.71% | NA | 1957 | 3 | 84.21 | 116 Segment, Retire | 2019 | 1 | 0 | 3 | 0 |  | 0 | 0
15973 | Anacortes H.P. Distribution System (Inlet 017-R-036) | 105 | 3 |  | 499 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 6.31% | 6.31% | 1973 | 73.4 | 52.31 | 116 Segment, Replace | 2019 | 1 | 1 | 0 | 73.4 |  | 0 | 0
29320 | 4" North Texas Rd H.P. Line | 250 | 3 |  | 933 | 100 | 66 | 250 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1980 | 83.9 | 50.53 | 116 Segment, Replace | 2021 | 1 | 1 | 0 | 83.9 |  | 0 | 0
14788 | 4" Sedro-Woolley H.P. Line | 100 | 3 |  | 877 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 3.42% | 2.71% | 1968 | 1902.2 | 57.42 | 116 Segment, Pressure Test | 2018 | 1 | 0 | 1902.2 | 0 |  | 0 | 0
11C2330 | Anacortes H.P. Distribution System | 105 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 3.37% | NA | 1959 | 70.4 | 62.87 | 116 Segment, Retire | 2020 | 1 | 0 | 70.4 | 0 |  | 0 | 0
11C2626 | Anacortes H.P. Distribution System | 105 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 3.37% | 3.37% | 1959 | 134.1 | 63.87 | 116 Segment, Replace | 2019 | 1 | 0 | 134.1 | 0 |  | 0 | 0
9801 | Anacortes H.P. Distribution System | 105 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 3.37% | 3.37% | 1966 | 112 | 56.87 | 116 Segment, Replace | 2019 | 1 | 0 | 112 | 0 |  | 0 | 0
14373 | Anacortes H.P. Distribution System | 105 | 3 |  | 933 | 100 | 71 | 1440 |  | 71 |  | NA | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 2.31% | 3.37% | 1968 | 1 | 44.87 | 116 Segment, Retire | 2020 | 1 | 0 | 1 | 0 |  | 0 | 0
1703 | Anacortes H.P. Distribution System | 105 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 10.04% | 7.71% | 1956 | 9849.9 | 104.04 | 116 Segment, Replace | 2018-2019 | 1 | 0 | 9849.9 | 0 |  | 0 | 0
21357 | Inlet 017-R-003 | 250 | 4 |  | 399 | 118 | 78 | 250 |  | 78 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 6.28% | 1973 | 12.4 | 68.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 12.4 |  | 0 | 0
G0082481 | Inlet 017-R-005 | 250 | 3 |  | 499 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 15.02% | 15.02% | 2007 | 21.4 | 49.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 21.4 |  | 0 | 0
23666 | Inlet 017-R-042 | 105 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 2.31% | NA | 1975 | 14 | 34.31 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 14 |  | 0 | 0
28930 | Inlet 017-R-070 | 105 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 2.31% | NA | 1981 | 41.7 | 31.31 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 41.7 |  | 0 | 0
19026 | Main Stub (017-R-054) | 400 | 3 |  | 933 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 12.85% | 12.85% | 1971 | 1 | 64.85 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 1 |  | 0 | 0
290015 | HPSS 290015 | 500 | 3 |  | 1214 | 250 | 166 | UNKV |  | 166 |  |  | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 12.35% | NA | 1991 | 20 | 64.35 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 20 |  | 0 | 0
25373 | Inlet 017-R-062 | 400 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 10.05% | 10.05% | 1978 | 42.8 | 58.55 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 42.8 |  | 0 | 0
620046 | HPSS 620046 | 400 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 10.05% | NA | 2007 | 21 | 44.05 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
621013 | HPSS 621013 | 400 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 10.05% | NA | 2010 | 11 | 42.55 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
20449 | Inlet 017-R-165 | 400 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1972 | 38.5 | 51.31 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 38.5 |  | 0 | 0
26782 | Inlet 017-R-068 | 400 | 3 |  | 1361 | 115 | 82 | 1200 |  | 82 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1979 | 8 | 47.81 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
36693 | Inlet 017-R-085 | 360 | 3 |  | 1361 | 375 | 250 | 1440 |  | 250 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 7.93% | 7.93% | 1989 | 33.9 | 41.93 | Addressed w/ 116 Segment | 2021 | 1 | 1 | 0 | 33.9 |  | 0 | 0
21175 | Inlet 017-R-019 | 249 | 3 |  | 877 | 110 | 73 | 720 |  | 73 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.51% | 6.75% | 1975 | 23.5 | 53.51 | Addressed w/ 116 Segment | 2017 | 1 | 1 | 0 | 23.5 |  | 0 | 0
25828 | 2" Gibralter Rd H.P. Line | 250 | 3 |  | 933 | 120 | 80 | 1440 |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1978 | 4464.2 | 59.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 4464.2 |  | 0 | 0
381300 | HPSS 381300 | 249 | 3 |  | 933 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.00% | NA | 1967 | 193.6 | 60.5 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 193.6 | 0 |  | 0 | 0
440108 | HPSS 440108 | 249 | 3 |  | 933 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.00% | 8.00% | 1986 | 201 | 48.5 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 201 |  | 0 | 0
36580 | Inlet 017-R-084 | 360 | 3 |  | 1361 | 110 | 73 | 1440 |  | 73 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 7.93% | NA | 1989 | 26 | 41.93 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 26 |  | 0 | 0
57392 | Inlet 017-R-132 | 360 | 3 |  | 2260 | 110 | 73 | 1200 |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 4.78% | NA | 1991 | 19.2 | 28.78 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 19.2 |  | 0 | 0
626250 | HPSS 626250 | 400 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1969 | 15 | 57.24 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 15 | 0 |  | 0 | 0
702000 | HPSS 702000 | 400 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1969 | 37.6 | 57.24 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 37.6 | 0 |  | 0 | 0
626300 | HPSS 626300 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1971 | 42.1 | 54.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 42.1 |  | 0 | 0
626908 | HPSS 626908 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1971 | 15.9 | 54.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 15.9 |  | 0 | 0
626550 | HPSS 626550 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1972 | 10 | 54.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 10 |  | 0 | 0
626900 | HPSS 626900 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1972 | 16.2 | 54.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 16.2 |  | 0 | 0
641136 | HPSS 641136 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1972 | 2.2 | 54.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 2.2 |  | 0 | 0
646205 | HPSS 646205 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1972 | 48.7 | 54.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 48.7 |  | 0 | 0
646210 | HPSS 646210 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1972 | 54.1 | 54.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 54.1 |  | 0 | 0
646211 | HPSS 646211 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1972 | 6 | 54.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 6 |  | 0 | 0
626915 | HPSS 626915 | 400 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1973 | 61.8 | 53.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 61.8 |  | 0 | 0
629100 | HPSS 629100 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1973 | 3.5 | 53.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 3.5 |  | 0 | 0
646305 | HPSS 646305 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1973 | 54.4 | 53.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 54.4 |  | 0 | 0
629066 | HPSS 629066 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1974 | 32 | 53.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 32 |  | 0 | 0
645252 | HPSS 645252 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1974 | 19.6 | 53.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 19.6 |  | 0 | 0
646064 | HPSS 646064 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NO | YES | 7.74% | 5.31% | 1975 | 15 | 52.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 15 |  | 0 | 0
646448 | HPSS 646448 | 400 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1977 | 82 | 51.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 82 |  | 0 | 0
626525 | HPSS 626525 | 400 | 3 |  | 1549 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1979 | 15 | 50.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 15 |  | 0 | 0
626909 | HPSS 626909 | 400 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1983 | 15 | 48.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
626620 | HPSS 626620 | 400 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1986 | 10 | 47.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
629065 | HPSS 629065 | 400 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1986 | 24 | 47.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 24 |  | 0 | 0
646121 | HPSS 646121 | 400 | 3 |  | 1549 | 350 | 233 | UNKV |  | 233 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1986 | 60 | 47.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 60 |  | 0 | 0
646601 | HPSS 646601 | 400 | 3 |  | 1549 | 350 | 233 | UNKV |  | 233 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1986 | 69.6 | 47.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 69.6 |  | 0 | 0
647502 | HPSS 647502 | 400 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1986 | 68.8 | 47.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 68.8 |  | 0 | 0
626916 | HPSS 626916 | 400 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1989 | 58.8 | 45.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 58.8 |  | 0 | 0
646005 | HPSS 646005 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1989 | 17.3 | 45.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 17.3 |  | 0 | 0
626201 | HPSS 626201 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1990 | 24.9 | 45.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 24.9 |  | 0 | 0
626825 | HPSS 626825 | 400 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1990 | 61.4 | 45.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 61.4 |  | 0 | 0
620500 | HPSS 620500 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 43 | 44.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
626824 | HPSS 626824 | 400 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 196.5 | 44.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 196.5 |  | 0 | 0
700009 | HPSS 700009 | 400 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1994 | 86.6 | 43.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 86.6 |  | 0 | 0
646602 | HPSS 646602 | 400 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 102 | 43.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 102 |  | 0 | 0
700850 | HPSS 700850 | 400 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1999 | 18 | 40.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
700010 | HPSS 700010 | 400 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 2002 | 178.2 | 40.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 178.2 |  | 0 | 0
G0068787 | Inlet 017-R-159 | 400 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2003 | 16.6 | 38.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 16.6 |  | 0 | 0
8148450830 | HPSS 8148450830 | 400 | 3 |  | 1549 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2010 | 18 | 35.24 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
211700 | HPSS 211700 | 360 | 3 |  | 1549 | 110 | 78 | UNKV |  | 78 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1964 | 11.5 | 61.47 | Addressed w/ 116 Segment | 2017 | 1 | 0 | 11.5 | 0 |  | 0 | 0
214980 | HPSS 214980 | 360 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1965 | 2 | 60.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 2 | 0 |  | 0 | 0
475555 | HPSS 475555 | 360 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1966 | 100 | 60.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 100 | 0 |  | 0 | 0
300263 | HPSS 300263 | 360 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1967 | 19 | 58.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 19 | 0 |  | 0 | 0
211900 | HPSS 211900 | 360 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1969 | 1.2 | 56.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 1.2 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
300259 | HPSS 300259 | 360 | 3 |  | 1549 | 120 | 85 | UNKV |  | 85 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1970 | 61.7 | 55.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 61.7 | 0 |  | 0 | 0
20908 | HPSS 20908 | 360 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1981 | 58.4 | 48.97 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 58.4 |  | 0 | 0
211816 | HPSS 211816 | 360 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1990 | 49.8 | 44.47 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 49.8 |  | 0 | 0
380049 | HPSS 380049 | 360 | 3 |  | 1549 | 345 | 230 | NA |  | 230 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 6.97% | NA | 1991 | 10 | 43.97 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 10 |  | 0 | 0
10006 | HPSS 10006 | 360 | 3 |  | 1549 | 160 | 106 | UNKV |  | 106 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1995 | 29 | 41.97 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 29 |  | 0 | 0
150090 | HPSS 150090 | 360 | 3 |  | 1549 | 100 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 2009 | 5.1 | 34.97 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 5.1 |  | 0 | 0
557250 | HPSS 560822 | 250 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1959 | 8 | 65.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 8 | 0 |  | 0 | 0
557200 | HPSS 557200 | 250 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1963 | 6.9 | 61.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 6.9 | 0 |  | 0 | 0
25451 | Inlet 017-R-008 | 250 | 4 |  | 954 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1978 | 12.4 | 51.78 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 12.4 |  | 0 | 0
560710 | HPSS 560710 | 250 | 3 |  | 1193 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1998 | 1 | 39.78 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 1 |  | 0 | 0
381135 | HPSS 381135 | 249 | 3 |  | 1193 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 6.26% | 6.26% | 1968 | 156 | 57.76 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 156 | 0 |  | 0 | 0
19949 | Inlet 017-R-052 | 400 | 3 |  | 2123 | 100 | 66 | 1200 |  | 66 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 5.65% | NA | 1972 | 49.2 | 48.15 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 49.2 |  | 0 | 0
G0078890 | Inlet 017-R-146 | 175 | 3 |  | 933 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 5.62% | NA | 2005 | 10.1 | 35.62 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10.1 |  | 0 | 0
497690 | HPSS 497690 | 250 | 4 |  | 1239 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1957 | 5 | 59.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 5 | 0 |  | 0 | 0
555810 | HPSS 555810 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1957 | 10 | 57.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 10 | 0 |  | 0 | 0
557000 | HPSS 557000 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1957 | 11.1 | 57.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 11.1 | 0 |  | 0 | 0
557400 | HPSS 557400 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1957 | 4 | 57.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 4 | 0 |  | 0 | 0
557500 | HPSS 557500 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1964 | 7 | 50.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 7 | 0 |  | 0 | 0
555595 | HPSS 555595 | 250 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1967 | 5 | 47.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 5 | 0 |  | 0 | 0
557395 | HPSS 557395 | 250 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1967 | 8 | 47.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 8 | 0 |  | 0 | 0
558000 | HPSS 558000 | 250 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1967 | 3 | 47.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 3 | 0 |  | 0 | 0
555805 | HPSS 555805 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1968 | 81.1 | 46.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 81.1 | 0 |  | 0 | 0
557510 | HPSS 557510 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 11.1 | 46.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 11.1 | 0 |  | 0 | 0
557440 | HPSS 557440 | 250 | 3 |  | 1549 | 50 | 35 | NA |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1969 | 22.7 | 45.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 22.7 | 0 |  | 0 | 0
557210 | HPSS 560572 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1970 | 12 | 44.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 12 | 0 |  | 0 | 0
555860 | HPSS 555860 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1972 | 10 | 42.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
557515 | HPSS 557515 | 250 | 3 |  | 1549 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1979 | 9 | 38.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
59254 | HPSS 555710 | 250 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1989 | 10 | 33.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
126009 | HPSS 126009 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 88 | 32.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 88 |  | 0 | 0
10098 | HPSS 10098 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1993 | 228.2 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 228.2 |  | 0 | 0
126004 | HPSS GG008544 | 250 | 3 |  | 1549 | 263 | 175 | UNKV |  | 175 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 91 | 31.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 91 |  | 0 | 0
126007 | HPSS 126007 | 250 | 3 |  | 1549 | 263 | 175 | UNKV |  | 175 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1994 | 139.3 | 32.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 139.3 |  | 0 | 0
123520 | HPSS 123520 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 145 | 31.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 145 |  | 0 | 0
126012 | HPSS 126012 | 250 | 3 |  | 1549 | 263 | 175 | UNKV |  | 175 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 71 | 30.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 71 |  | 0 | 0
560452 | HPSS 560452 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 57.1 | 30.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 57.1 |  | 0 | 0
19092 | HPSS 19092 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1996 | 469.8 | 31.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 469.8 |  | 0 | 0
19100 | HPSS 19100 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1996 | 240 | 31.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 240 |  | 0 | 0
570326 | HPSS 570326 | 250 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 38.8 | 29.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 38.8 |  | 0 | 0
8266300269 | HPSS 8266300269 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 10 | 28.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
570413 | HPSS 570413 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 55.1 | 28.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
570271 | HPSS 570271 | 250 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 21 | 25.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
380505 | HPSS 380505 | 249 | 3 |  | 1549 | 350 | 233 | NA |  | 233 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.82% | NA | 1994 | 63 | 31.32 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 63 |  | 0 | 0
562501877 | HPSS 562501877 | 175 | 3 |  | 1193 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 4.40% | NA | 2012 | 42.1 | 21.9 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 42.1 |  | 0 | 0
420009 | HPSS 420009 | 151 | 3 |  | 1193 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.80% | NA | 1966 | 7 | 47.3 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 7 | 0 |  | 0 | 0
G0078221 | Anacortes H.P. Distribution System | 105 | 3 |  | 933 | 100 | 1 | UNKV |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 3.37% | 3.37% | 2005 | 263 | 25.37 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 263 |  | 0 | 0
12568 | Inlet 017-R-161 | 151 | 3 |  | 1361 | 100 | 66 | 1440 |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 3.33% | NA | 1967 | 46.9 | 41.83 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 46.9 | 0 |  | 0 | 0
570435 | HPSS 570435 | 250 | 3 |  | 2260 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2000 | 17 | 22.82 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
420012 | HPSS 420012 | 151 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1969 | 39.9 | 43.42 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 39.9 | 0 |  | 0 | 0
420003 | HPSS 420003 | 151 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.92% | NA | 1973 | 42 | 39.92 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
420004 | HPSS 420004 | 151 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.92% | 2.92% | 1974 | 44 | 39.42 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
420900 | HPSS 420900 | 151 | 3 |  | 1549 | 225 | 150 | NA |  | 150 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 2.92% | 2.92% | 1991 | 1095.1 | 38.42 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 1095.1 |  | 0 | 0
10820 | HPSS 10820 | 105 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.03% | NA | 1958 | 0.1 | 53.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 0.1 | 0 |  | 0 | 0
10830 | HPSS 10830 | 105 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1958 | 19.1 | 53.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 19.1 | 0 |  | 0 | 0
10859 | HPSS 10859 | 105 | 3 |  | 1549 | 105 | 75 | UNKV |  | 75 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1966 | 11 | 45.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 11 | 0 |  | 0 | 0
21035 | HPSS 21035 | 105 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1967 | 50.4 | 44.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 50.4 | 0 |  | 0 | 0
10857 | HPSS 10857 | 105 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1968 | 20 | 43.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 20 | 0 |  | 0 | 0
10975 | HPSS 10975 | 105 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1968 | 29.3 | 43.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 29.3 | 0 |  | 0 | 0
10595 | HPSS 10595 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1970 | 16 | 41.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 16 | 0 |  | 0 | 0
10813 | HPSS 10813 | 105 | 3 |  | 1549 | 75 | 53 | UNKV |  | 53 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1970 | 25.4 | 41.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 25.4 | 0 |  | 0 | 0
10885 | HPSS 10885 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1971 | 11 | 40.03 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 11 |  | 0 | 0
10812 | HPSS 10812 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1973 | 44.6 | 39.03 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 44.6 |  | 0 | 0
5680000534 | HPSS 5680000534 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1974 | 16.7 | 38.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 16.7 |  | 0 | 0
10853 | HPSS 10853 | 105 | 3 |  | 1549 | 115 | 76 | UNKV |  | 76 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1979 | 16.7 | 36.03 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 16.7 |  | 0 | 0
10605 | HPSS 10605 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1980 | 16 | 35.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 16 |  | 0 | 0
10810 | HPSS 10810 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.03% | 2.03% | 1982 | 84.2 | 34.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 84.2 |  | 0 | 0
10808 | HPSS 10808 | 105 | 3 |  | 1549 | 150 | 100 | NA |  | 100 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.03% | NA | 1986 | 67.6 | 32.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 67.6 |  | 0 | 0
10840 | HPSS 10840 | 105 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1992 | 16 | 29.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 16 |  | 0 | 0
11768 | HPSS 11768 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1992 | 25 | 29.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 25 |  | 0 | 0
27032 | HPSS 27032 | 105 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1996 | 13 | 27.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 13 |  | 0 | 0
40022 | M&R 40022 | 360 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 12.75 | 0.375 | 24000 | 0.8 | YES | NO | YES | 34.41% | 15.15% | 1991 | 123.3 | 122.41 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 123.3 |  | 0 | 0
17363 | Inlet 017-R-051 | 105 | 3 |  | 2123 | 120 | 85 | 1440 |  | 85 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 1.48% | NA | 1970 | 73.7 | 36.98 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 73.7 | 0 |  | 0 | 0
31979 | Inlet 017-R-028 | 400 | 3 |  | 933 | 675 | 1 | 500 |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.81% | 12.85% | 1985 | 425.1 | 58.85 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 425.1 |  | 0 | 0
33937 | Main to HPSS 626912 | 400 | 3 |  | 933 | 750 | 1 | 250 |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.81% | 12.85% | 1986 | 134.8 | 58.35 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 134.8 |  | 0 | 0
602082 | HPSS 602082 | 400 | 3 |  | 2112 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.154 | 24000 | 0.6 | YES | NA | NA | 5.68% | NA | 2005 | 27.4 | 35.68 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 27.4 |  | 0 | 0
56133 | Inlet 017-R-124 | 360 | 3 |  | 1361 | 600 | 400 | 250 |  | 250 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 7.93% | NA | 1998 | 29.1 | 32.43 | Expose/Verify/Replace | 2024-2028 | 1 | 1 | 0 | 29.1 |  | 0 | 0
58203 | Inlet 017-R-130 | 400 | 3 |  | 933 | 750 | 500 | 275 |  | 275 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 9.88% | 12.85% | 1999 | 164.9 | 46.85 | Expose/Verify/Replace | 2024-2028 | 1 | 1 | 0 | 164.9 |  | 0 | 0
34198 | Inlet 017-R-078 | 175 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 5.62% | NA | 1986 | 0 | 60.12 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 0 |  | 0 | 0
37799 | 017-V-042 | 249 | 3 |  | 877 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.51% | 6.75% | 1992 | 30.3 | 56.01 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 30.3 |  | 0 | 0
170354 | Inlet 017-R-157 | 500 | 3 |  | 1106 | 100 | 66 | 720 |  | 66 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 13.56% | 13.56% | 2009 | 42.1 | 42.56 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 42.1 |  | 0 | 0
40025 | 017-R-090 | 360 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 16 | 0.375 | 52000 | 0.8 | YES | YES | YES | 26.43% | 34.41% | 1991 | 196.5 | 122.41 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 196.5 |  | 0 | 0
217470 | 8" Anacortes Transmission Line | 360 | 3 |  | 1045 | 771 | 514 | 250 |  | 250 |  | X | UNVALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 11.94% | 13.78% | 2014 | 928 | 60.28 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 928 |  | 0 | 0
37800 | 017-V-047, 048 | 249 | 3 |  | 1106 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 6.75% | 6.75% | 1992 | 27 | 54.25 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 27 |  | 0 | 0
177232 | 017-R-166, 017-O-006 | 250 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 18.35% | 18.35% | 1989 | 723.9 | 81.35 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 723.9 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
34371 | Inlet 017-R-082 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 1987 | 10.1 | 74.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 10.1 |  | 0 | 0
G0075193 | 4" Mount Vernon Gate H.P. Line | 250 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 15.02% | 15.02% | 2005 | 329.2 | 66.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 329.2 |  | 0 | 0
G0075199 | 017-R-167 | 250 | 3 |  | 499 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 2005 | 116.8 | 66.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 116.8 |  | 0 | 0
31324 | Inlet 017-R-004 | 250 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1957 | 7.3 | 84.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 7.3 | 0 |  | 0 | 0
G0072371 (R-143) | Inlet 017-R-143 | 250 | 3 |  | 933 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 2004 | 40.2 | 53.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 40.2 |  | 0 | 0
11C7157 | 017-V-003, 004 | 360 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 34.41% | 13.78% | 1963 | 29.2 | 158.91 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 29.2 | 0 |  | 0 | 0
10900 | HPSS 10900 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1960 | 28 | 60.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 28 | 0 |  | 0 | 0
60133 | Inlet 017-R-134 | 360 | 3 |  | 544 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 26.43% | 26.43% | 2001 | 85.8 | 98.43 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 85.8 |  | 0 | 0
35840 (R-41) | Inlet 017-R-041 | 360 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 11.57% | 11.57% | 1957 | 15 | 94.57 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 15 | 0 |  | 0 | 0
55633 | 017-R-121 | 360 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 11.57% | 11.57% | 1999 | 16.6 | 64.57 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 16.6 |  | 0 | 0
1880 | 017-R-047 | 360 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 34.41% | 34.41% | 1956 | 11.2 | 155.91 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 11.2 | 0 |  | 0 | 0
Stub (17206) | Main Stub | 400 | 3 |  | 1456 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.133 | 24000 | 0.6 | YES | NA | NA | 8.24% | NA | 1972 | 2 | 69.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 2 |  | 0 | 0
20510 | HPSS 20510 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1957 | 51.3 | 63.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 51.3 | 0 |  | 0 | 0
2080 | 017-R-089 to 8" March Point Transmission Line | 360 | 3 |  | 544 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 26.43% | 26.43% | 1958 | 177.5 | 131.93 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 177.5 | 0 |  | 0 | 0
2934227682 | HPSS 2934227682 | 400 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1969 | 51.2 | 72.24 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 51.2 | 0 |  | 0 | 0
58210 | Inlet 017-R-130 | 400 | 3 |  | 1771 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 1.66 | 0.14 | 35000 | 0.6 | NO | NO | YES | 6.78% | 6.78% | 2000 | 359.1 | 51.28 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 359.1 |  | 0 | 0
10800 | HPSS 10800 | 105 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.03% | NA | 1958 | 36.9 | 62.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 36.9 | 0 |  | 0 | 0
13C8489 | Inlet 017-R-024 | 360 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 21.63% | 21.63% | 1965 | 8.6 | 109.13 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 8.6 | 0 |  | 0 | 0
420139 | HPSS 420139 | 151 | 3 |  | 1549 | 750 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 2006 | 59.2 | 23.42 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 59.2 |  | 0 | 0
290045 | HPSS 290045 | 175 | 3 |  | 1456 | 750 | 1 | NA |  | 1 |  |  | UNVALID | 1.315 | 0.133 | 24000 | 0.6 | NO | NA | NA | 3.60% | NA | 2009 | 12.9 | 22.6 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12.9 |  | 0 | 0
602297 | HPSS 602297 | 400 | 3 |  | 1549 | 750 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1999 | 19 | 40.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
602218 | HPSS 7169300838 | 400 | 3 |  | 1549 | 750 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | YES | YES | 5.31% | 7.74% | 1999 | 7.8 | 40.74 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 7.8 |  | 0 | 0
420660 | HPSS 0420660 | 500 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 16.06% | NA | 1992 | 51.3 | 82.56 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 51.3 |  | 0 | 0
20840 | HPSS 20840 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1958 | 122.4 | 63.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 122.4 | 0 |  | 0 | 0
197546 | 017-R-167 | 250 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 15.02% | 15.02% | 2012 | 71.1 | 61.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 71.1 |  | 0 | 0
23477 | Inlet 017-R-060 | 400 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 12.85% | NA | 1969 | 7 | 83.85 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 7 | 0 |  | 0 | 0
11C4752 | Inlet 017-R-038 | 360 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 11.57% | NA | 1961 | 39.3 | 90.57 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 39.3 | 0 |  | 0 | 0
12C9577 | Inlet 017-R-016 | 360 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 11.57% | NA | 1965 | 9 | 86.57 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 9 | 0 |  | 0 | 0
14851 | 017-R-012 | 360 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 11.57% | NA | 1968 | 33.2 | 83.57 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 33.2 | 0 |  | 0 | 0
15491 | Inlet 017-R-001 | 360 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 11.57% | NA | 1969 | 4 | 82.57 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 4 | 0 |  | 0 | 0
0 | Service Stub | 360 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 9.05% | 6.97% | 1960 | 6 | 82.55 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 6 | 0 |  | 0 | 0
16051 | Inlet 017-R-063 | 400 | 3 |  | 1361 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1969 | 96.2 | 69.31 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 96.2 | 0 |  | 0 | 0
28823 | Inlet 017-R-066 | 249 | 3 |  | 877 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.51% | 6.75% | 1982 | 25 | 61.01 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 25 |  | 0 | 0
497600 | HPSS 497611 | 250 | 4 |  | 1239 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 1 | 44.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 1 |  | 0 | 0
61 | Inlet M&R 37429, 09020 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 4.84% | 1958 | 113 | 84.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 113 | 0 |  | 0 | 0
71C5927 | Inlet 017-R-007 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1962 | 76.4 | 79.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 76.4 | 0 |  | 0 | 0
10600 | HPSS 10600 | 105 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.03% | NA | 1959 | 106 | 62.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 106 | 0 |  | 0 | 0
12c8363 | Inlet 017-R-013 | 360 | 3 |  | 1361 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NO | YES | 7.93% | 7.93% | 1964 | 14.5 | 73.43 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 14.5 | 0 |  | 0 | 0
626623 | HPSS 626623 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1969 | 25 | 72.24 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 25 | 0 |  | 0 | 0
210296 | HPSS 210296 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 1 | YES | NO | NO | 6.97% | 5.08% | 1964 | 24.3 | 74.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 24.3 | 0 |  | 0 | 0
643500 | HPSS 643500 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1973 | 45 | 68.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 45 |  | 0 | 0
620812 | HPSS 628012 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1992 | 6.9 | 59.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 6.9 |  | 0 | 0
622201 | HPSS 622201 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 15 | 58.74 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 15 |  | 0 | 0
620311 | HPSS 620311 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2002 | 18 | 54.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 18 |  | 0 | 0
10027 | HPSS 10027 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1961 | 73.1 | 79.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 73.1 | 0 |  | 0 | 0
10028 | HPSS 10028 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1961 | 48 | 89.47 | Addressed w/ 116 Segment | 2018 | 1 | 0 | 48 | 0 |  | 0 | 0
300260 | HPSS 300260 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1962 | 1 | 78.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 1 | 0 |  | 0 | 0
1520000001 | HPSS 1520000001 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1965 | 10 | 75.47 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 10 | 0 |  | 0 | 0
10878 | HPSS 10878 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1971 | 11.3 | 68.97 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 11.3 |  | 0 | 0
21000 | Inlet 017-R-017 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 6.97% | 6.97% | 1973 | 10.9 | 67.97 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 10.9 |  | 0 | 0
60145 | HPSS 60145 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 2001 | 7.3 | 53.97 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 7.3 |  | 0 | 0
211701 | HPSS 211701 | 360 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 2004 | 8 | 52.47 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 8 |  | 0 | 0
40026 | 017-R-091 | 500 | 3 |  | 975 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 12.75 | 0.375 | 42000 | 0.8 | NO | NO | YES | 20.24% | 18.93% | 1991 | 51.1 | 83.24 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 51.1 |  | 0 | 0
40024 | 017-R-089 | 500 | 3 |  | 811 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NA | NA | 24.64% | NA | 1991 | 23.1 | 87.64 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 23.1 |  | 0 | 0
21304 | Inlet 017-R-018 | 249 | 3 |  | 933 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | YES | YES | 6.75% | 8.00% | 1975 | 63.6 | 68 | Addressed w/ 116 Segment | 2017 | 1 | 1 | 0 | 63.6 |  | 0 | 0
497455 | HPSS 497455 | 250 | 4 |  | 954 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1957 | 10.9 | 84.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 10.9 | 0 |  | 0 | 0
555830 | HPSS 555830 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1960 | 6 | 79.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 6 | 0 |  | 0 | 0
555850 | HPSS 555850 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1960 | 5 | 79.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 5 | 0 |  | 0 | 0
557055 | Service Stub | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 6.28% | 4.84% | 1960 | 1 | 79.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 1 | 0 |  | 0 | 0
557100 | HPSS 557100 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1969 | 1 | 70.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 1 | 0 |  | 0 | 0
557260 | HPSS 557260 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1969 | 7 | 70.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 7 | 0 |  | 0 | 0
497700 | HPSS 497700 | 250 | 4 |  | 954 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 6.28% | 6.28% | 1994 | 177.6 | 59.78 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 177.6 |  | 0 | 0
490108 | HPSS 490108 | 250 | 4 |  | 954 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2005 | 8 | 53.28 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 8 |  | 0 | 0
490259 | HPSS 490259 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 6.28% | 6.28% | 2005 | 66.4 | 51.28 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 66.4 |  | 0 | 0
GG002457 | Air Liquide Acoustic Filter | 500 | 3 |  | 877 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 42000 | 0.8 | NO | NO | YES | 20.98% | 16.90% | 2002 | 203.8 | 79.48 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 203.8 |  | 0 | 0
18439 | Inlet 017-R-006 | 250 | 3 |  | 1361 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NA | NA | 5.51% | NA | 1971 | 63.1 | 63.51 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 63.1 |  | 0 | 0
195663 | Inlet 017-R-163 | 400 | 3 |  | 2260 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 5.31% | NA | 2012 | 16.4 | 42.81 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 16.4 |  | 0 | 0
3165827598 | HPSS 3165827598 | 360 | 3 |  | 2123 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 5.08% | NA | 2012 | 9 | 42.58 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 9 |  | 0 | 0
555845 | HPSS 555845 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1957 | 6 | 66.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 6 | 0 |  | 0 | 0
557450 | HPSS 557450 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 6.28% | 1957 | 5.5 | 82.78 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 5.5 | 0 |  | 0 | 0
PRE-CNG | Inlet 017-R-135 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1957 | 8.1 | 66.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 8.1 | 0 |  | 0 | 0
150111 | HPSS 150111 | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 8.03% | 1958 | 1 | 83.53 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 1 | 0 |  | 0 | 0
40023 | M&R 40023 | 500 | 3 |  | 950 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 10.75 | 0.25 | 52000 | 0.8 | YES | NO | YES | 20.67% | 21.04% | 1991 | 115.9 | 85.04 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 115.9 |  | 0 | 0
555855 | HPSS 555855 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1989 | 18 | 42.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
128004 | HPSS 128004 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1994 | 67 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 67 |  | 0 | 0
555710 | HPSS 555710 | 250 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2000 | 3.5 | 37.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 3.5 |  | 0 | 0
570509 | HPSS 570509 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2001 | 30 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
570594 | HPSS 570594 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 27 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 27 |  | 0 | 0
18C6103 | Inlet 017-R-065 | 150 | 3 |  | 1456 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.315 | 0.133 | 24000 | 0.6 | NO | NA | NA | 3.09% | NA | 1963 | 7.9 | 58.59 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 7.9 | 0 |  | 0 | 0
420005 | HPSS 420005 | 151 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1965 | 7 | 56.42 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 7 | 0 |  | 0 | 0
420006 | HPSS 420006 | 151 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1965 | 45.9 | 56.42 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 45.9 | 0 |  | 0 | 0
420007 | HPSS 420007 | 151 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1965 | 43 | 56.42 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 43 | 0 |  | 0 | 0
420010 | HPSS 420010 | 151 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1965 | 47 | 56.42 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 47 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
20506 | HPSS 20506 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1961 | 49 | 59.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 49 | 0 |  | 0 | 0
10995 | Service Stub | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1963 | 36 | 57.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 36 | 0 |  | 0 | 0
2301000684 | HPSS 2301000684 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1964 | 18.1 | 56.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 18.1 | 0 |  | 0 | 0
10815 | HPSS 10815 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1965 | 17.2 | 55.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 0 | 17.2 | 0 |  | 0 | 0
7001000662 | HPSS 7001000662 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.03% | 2.03% | 1959 | 122 | 62.53 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 122 | 0 |  | 0 | 0
35043 | Inlet 017-R-083 | 500 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 16.06% | NA | 1988 | 4 | 74.56 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 4 |  | 0 | 0
10832 | HPSS 10832 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1988 | 40.8 | 40.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 40.8 |  | 0 | 0
10860 | HPSS 10860 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1990 | 16.4 | 39.53 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 16.4 |  | 0 | 0
10855 | HPSS 1780000537 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 2001 | 15.1 | 34.03 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 15.1 |  | 0 | 0
G0083238 | 017-V-182 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.03% | 2.03% | 2007 | 21 | 31.03 | Addressed w/ 116 Segment | 2018-2019 | 1 | 1 | 0 | 21 |  | 0 | 0
10997 | HPSS 10997 | 105 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1965 | 45 | 55.53 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 45 | 0 |  | 0 | 0
G0071167 | 6" North Oak Harbor H.P. Line (017-V-125) | 400 | 3 |  | NA | NA | NA | 720 |  | 720 | X |  | UNVALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2003 | 0 | 17 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
G0083870 | Inlet 017-R-175 | 400 | 3 |  | NA | NA | NA | 720 |  | 720 | X |  | UNVALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2009 | 0 | 14 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
32166 | Inlet 017-R-075 | 500 | 3 |  | 794 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 25.17% | 16.90% | 1985 | 40.8 | 76.17 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 40.8 |  | 0 | 0
G0080213 | Inlet 017-R-150 | 400 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 12.85% | NA | 2006 | 9 | 42.35 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 9 |  | 0 | 0
G0072195 | 017-V-157 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2004 | 0 | 16.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
170355 | Inlet 017-R-157 | 500 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2010 | 0 | 13.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
184723 | Inlet 017-R-161 | 151 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2011 | 0 | 13 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
201582 | Inlet 017-R-129 | 400 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2013 | 0 | 12 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
37190 | 8" March Point Transmission Line | 360 | 3 |  | 610 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 23.59% | 13.78% | 1989 | 132.1 | 77.59 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 132.1 | 1 | 0 | 132.1 |  | 1
G0067527 | 017-O-001 | 1000 | 3 |  | 1882 | 1500 | 1000 | 1440 |  | 1000 | X | X | VALID | 12.75 | 0.5 | 60000 | 0.8 | NO | NO | YES | 21.25% | 21.25% | 2004 | 84.9 | 52.75 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 84.9 | 1 | 0 | 84.9 |  | 1
188455-T | 16" Fredonia Transmission Line (017-V-208, 209, 210) | 500 | 3 |  | 975 | 750 | 500 | 720 |  | 500 | X | X | VALID | 16 | 0.375 | 52000 | 0.8 | NO | YES | YES | 20.51% | 20.51% | 2012 | 75.2 | 52.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 75.2 | 1 | 0 | 75.2 |  | 1
188456-T | 16" Fredonia Transmission Line (017-V-204) | 500 | 3 |  | 975 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 16 | 0.375 | 52000 | 0.8 | NO | NO | YES | 20.51% | 20.51% | 2012 | 42 | 48.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 42 | 1 | 0 | 42 |  | 1
16052 | 6" Whidbey Island H.P. Line | 400 | 3 |  | 811 | 700 | 466 | NA |  | 466 | X | NA | VALID | 6.625 | 0.188 | 42000 | 0.8 | NO | NO | YES | 19.72% | 16.78% | 1969 | 28499.5 | 85.72 | Accept Most Stringent Criteria | -- | 1 | 0 | 28499.5 | 0 | 1 | 28499.5 | 0 | 1
G0082548 | Inlet 017-R-154 | 960 | 3 |  | 1453 | 1520 | 1013 | 1440 |  | 1013 | X | X | VALID | 4.5 | 0.337 | 42000 | 0.6 | NO | NO | YES | 17.63% | 19.81% | 2009 | 79 | 43.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 79 | 1 | 0 | 79 |  | 1
16055 | 6" Whidbey Island H.P. Line | 400 | 3 |  | 953 | 700 | 466 | NA |  | 466 | X | NA | VALID | 6.625 | 0.188 | 42000 | 0.8 | NO | NO | YES | 16.78% | 16.78% | 1969 | 38448.8 | 83.78 | Accept Most Stringent Criteria | -- | 1 | 0 | 38448.8 | 0 | 1 | 38448.8 | 0 | 1
188455 | 12" Anacortes H.P. Line (017-V-211) | 500 | 3 |  | 1193 | 750 | 500 | 720 |  | 500 | X | X | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | YES | YES | 16.35% | 16.35% | 2012 | 4.8 | 42.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4.8 | 1 | 0 | 4.8 |  | 1
188456 | 12" Anacortes H.P. Line (017-V-202, 203) | 500 | 3 |  | 1223 | 750 | 500 | 720 |  | 500 | X | X | VALID | 12.75 | 0.375 | 52000 | 0.8 | NO | NO | YES | 16.35% | 16.35% | 2012 | 35.4 | 38.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35.4 | 1 | 0 | 35.4 |  | 1
174254 | 8" Anacortes Transmission Line | 360 | 3 |  | 906 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.188 | 52000 | 0.8 | NO | YES | YES | 15.88% | 9.27% | 2010 | 511.4 | 48.38 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 511.4 | 1 | 0 | 511.4 |  | 1
170067 | 4" Mount Vernon H.P. Line | 250 | 3 |  | 499 | 650 | 433 | 720 |  | 433 | X | X | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 2009 | 236.6 | 44.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 236.6 | 1 | 0 | 236.6 |  | 1
50393 | 8" Anacortes Transmission Line | 360 | 3 |  | 802 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.322 | 35000 | 0.8 | NO | NO | YES | 13.78% | 17.95% | 1998 | 26.2 | 67.45 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 26.2 | 1 | 0 | 26.2 |  | 1
53023 | Inlet 017-R-031 | 360 | 3 |  | 1056 | 750 | 500 | NA |  | 500 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 13.63% | 12.17% | 1997 | 6.4 | 43.63 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6.4 | 1 | 0 | 6.4 |  | 1
57409 | Inlet 017-R-128 | 400 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NO | YES | 12.85% | 8.81% | 2000 | 26.4 | 45.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 26.4 | 1 | 0 | 26.4 |  | 1
33699 | 6" Mount Vernon H.P. Line | 250 | 3 |  | 499 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 15.02% | 1989 | 12840 | 68.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 12840 | 1 | 0 | 12840 |  | 1
186092 | 8" Anacortes Transmission Line | 360 | 3 |  | 1045 | 840 | 560 | 720 |  | 560 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 11.94% | 13.78% | 2011 | 129.3 | 57.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 129.3 | 1 | 0 | 129.3 |  | 1
186778 | Outlet 017-R-162 | 360 | 3 |  | 1045 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 11.94% | 13.78% | 2012 | 30 | 36.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 30 | 1 | 0 | 30 |  | 1
G0080886 | Inlet 017-R-025 | 360 | 3 |  | 933 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 11.57% | 11.57% | 2006 | 18.7 | 41.07 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 18.7 | 1 | 0 | 18.7 |  | 1
186779 | Inlet 017-R-162 | 500 | 3 |  | 1106 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 52000 | 0.6 | NO | NO | YES | 11.51% | 13.56% | 2012 | 134.8 | 37.06 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 134.8 | 1 | 0 | 134.8 |  | 1
34326 | Inlet 017-R-081 | 500 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 11.02% | 11.02% | 1987 | 133.4 | 47.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 133.4 | 1 | 0 | 133.4 |  | 1
209739 | Inlet 017-R-173 | 500 | 3 |  | 933 | 790 | 526 | 720 |  | 526 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 11.02% | 16.06% | 2014 | 333.9 | 42.56 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 333.9 | 1 | 0 | 333.9 |  | 1
53021 | 8" Anacortes H.P. Line (017-V-089) | 360 | 3 |  | 933 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | YES | YES | 9.76% | 13.78% | 1997 | 20.5 | 47.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20.5 | 1 | 0 | 20.5 |  | 1
52583 | Inlet 017-R-031 (Anacortes CM) | 360 | 3 |  | 751 | 750 | 500 | NA |  | 500 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 9.76% | 14.38% | 1997 | 20.4 | 44.38 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20.4 | 1 | 0 | 20.4 |  | 1
G0072371 (R-141 IN) | Inlet 017-R-141 | 360 | 3 |  | 1106 | 735 | 490 | 720 |  | 490 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 9.76% | 12.17% | 2004 | 48.1 | 38.67 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 48.1 | 1 | 0 | 48.1 |  | 1
16053 | 6" Whidbey Island H.P. Line | 400 | 3 |  | 1183 | 700 | 466 | NA |  | 466 | X | NA | VALID | 6.625 | 0.28 | 52000 | 0.8 | NO | NO | YES | 9.10% | 13.52% | 1969 | 15861.5 | 75.52 | Accept Most Stringent Criteria | -- | 1 | 0 | 15861.5 | 0 | 1 | 15861.5 | 0 | 1
189777 | 6" Whidbey Island H.P. Line (017-V-213) | 400 | 3 |  | 1193 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.28 | 52000 | 0.8 | NO | YES | YES | 9.10% | 10.05% | 2013 | 12.3 | 36.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 12.3 | 1 | 0 | 12.3 |  | 1
220939 | Inlet 017-R-175 | 400 | 3 |  | 2269 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 1 | NO | NO | NO | 8.81% | 8.81% | 2015 | 3 | 22.81 | No Action Needed | -- | 1 | 1 | 0 | 3 | 1 | 0 | 3 |  | 1
G0079640 | Inlet 017-R-147 | 400 | 3 |  | 1361 | 800 | 533 | 1440 |  | 533 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 2006 | 20 | 29.31 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20 | 1 | 0 | 20 |  | 1
G0070011 | Inlet 017-R-140 | 400 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 2003 | 28.9 | 30.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 28.9 | 1 | 0 | 28.9 |  | 1
191622 | Inlet 017-R-165 | 400 | 3 |  | 933 | 750 | 500 | 720 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.81% | 12.85% | 2013 | 55 | 38.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 55 | 1 | 0 | 55 |  | 1
15312 | 4" Mount Vernon H.P. Line | 250 | 3 |  | 877 | 470 | 335 | 720 |  | 335 | X | NA | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 8.03% | 1968 | 781.2 | 59.05 | Accept Most Stringent Criteria | -- | 1 | 0 | 781.2 | 0 | 1 | 781.2 | 0 | 1
33700 | 4" Mount Vernon H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 275 |  | 275 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.78% | 1987 | 6182.7 | 52.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6182.7 | 1 | 0 | 6182.7 |  | 1
44413 | 4" North Texas Rd H.P. Line | 250 | 3 |  | 877 | 820 | 546 | 720 |  | 546 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.78% | 1994 | 2439 | 46.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2439 | 1 | 0 | 2439 |  | 1
47569 | 4" Mount Vernon H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.78% | 1994 | 879.6 | 44.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 879.6 | 1 | 0 | 879.6 |  | 1
54633 | 4" Big Lake H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 8.45% | 1999 | 7673.8 | 46.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7673.8 | 1 | 0 | 7673.8 |  | 1
G0067635 | 4" Arlington H.P. Line (Main to 017-R-137) | 249 | 3 |  | 877 | 750 | 500 | 275 |  | 275 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.51% | 6.75% | 2003 | 2330.8 | 42.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2330.8 | 1 | 0 | 2330.8 |  | 1
41858 | Inlet 017-R-096 | 360 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 7.93% | NA | 1992 | 22 | 35.43 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 22 | 1 | 0 | 22 |  | 1
42768 | Inlet 017-R-097 | 360 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 7.93% | NA | 1993 | 25.9 | 34.93 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 25.9 | 1 | 0 | 25.9 |  | 1
GG011832 | 6” North Anacortes H.P. Line | 105 | 3 |  | 544 | 375 | 250 | NA |  | 250 | X | X | VALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 7.71% | 7.71% | 1995 | 5223.2 | 47.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5223.2 | 1 | 0 | 5223.2 |  | 1
82379 | Inlet 017-R-151 | 105 | 3 |  | 544 | 375 | 250 | 720 |  | 250 | X | X | VALID | 6.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 7.71% | NA | 1995 | 22.3 | 37.71 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 22.3 | 1 | 0 | 22.3 |  | 1
220566 | Inlet 017-R-174 | 400 | 3 |  | 1361 | 760 | 506 | 1440 |  | 506 | X | X | VALID | 2.375 | 0.188 | 35000 | 0.8 | NO | NO | YES | 7.22% | 8.81% | 2015 | 93.9 | 24.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 93.9 | 1 | 0 | 93.9 |  | 1
G0072368 | 4" South Anacortes H.P. Line | 250 | 3 |  | 499 | 600 | 400 | 275 |  | 275 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 7.12% | 15.02% | 2004 | 6905.4 | 55.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6905.4 | 1 | 0 | 6905.4 |  | 1
2526100597 | HPSS 2526100597 | 500 | 3 |  | 3539 | 850 | 566 | 740 |  | 566 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NO | NO | 7.06% | 7.06% | 2012 | 162.1 | 23.56 | No Action Needed | -- | 1 | 1 | 0 | 162.1 | 1 | 0 | 162.1 |  | 1
G0072371 (R-141 OUT) | Outlet 017-R-141 | 250 | 3 |  | 1106 | 735 | 490 | NA |  | 490 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NA | NA | 6.78% | NA | 2004 | 13.6 | 28.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 13.6 | 1 | 0 | 13.6 |  | 1
58169 | Inlet 017-R-129 | 400 | 3 |  | 1771 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 1.66 | 0.14 | 35000 | 0.6 | NO | NA | NA | 6.78% | NA | 2000 | 58.6 | 30.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 58.6 | 1 | 0 | 58.6 |  | 1
179240 | Inlet 017-R-160 | 400 | 3 |  | 1820 | 750 | 500 | 720 |  | 500 | X | X | VALID | 1.315 | 0.133 | 30000 | 0.6 | NO | NA | NA | 6.59% | NA | 2010 | 31.9 | 25.09 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 31.9 | 1 | 0 | 31.9 |  | 1
G0084755 | Inlet 017-R-053 | 400 | 3 |  | 2123 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 5.65% | NA | 2008 | 6.1 | 25.15 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6.1 | 1 | 0 | 6.1 |  | 1
172651 | Inlet 017-R-158 | 400 | 3 |  | 1193 | 800 | 533 | 720 |  | 533 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | YES | YES | 5.65% | 10.05% | 2010 | 60 | 37.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 60 | 1 | 0 | 60 |  | 1
227564 | Inlet 017-R-178 | 400 | 3 |  | 2123 | 750 | 500 | 720 |  | 500 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 5.65% | NA | 2015 | 57 | 21.65 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 57 | 1 | 0 | 57 |  | 1
2600824709 | HPSS 2600824709 | 400 | 3 |  | 3539 | 750 | 500 | 740 |  | 500 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NO | NO | 5.65% | 5.65% | 2016 | 32.4 | 19.15 | No Action Needed | -- | 1 | 1 | 0 | 32.4 | 1 | 0 | 32.4 |  | 1
48828 | 6" North Anacortes H.P. Line | 105 | 3 |  | 544 | 500 | 333 | 250 |  | 250 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 5.29% | 7.71% | 1995 | 4644.7 | 45.21 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4644.7 | 1 | 0 | 4644.7 |  | 1
53023 (OUT) | Outlet 017-R-031 | 105 | 3 |  | 811 | 275 | 183 | NA |  | 183 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NA | NA | 5.18% | NA | 1997 | 28.3 | 30.18 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 28.3 | 1 | 0 | 28.3 |  | 1
8467527976 | HPSS 8467527976 | 360 | 3 |  | 3539 | 770 | 513 | 740 |  | 513 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NO | NO | 5.08% | 5.08% | 2017 | 47 | 18.08 | No Action Needed | -- | 1 | 1 | 0 | 47 | 1 | 0 | 47 |  | 1
56629 | Inlet 017-R-126 | 151 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 4.85% | 4.85% | 2000 | 151.6 | 28.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 151.6 | 1 | 0 | 151.6 |  | 1
29141 | 2" Fredonia H.P. Line | 175 | 3 |  | 933 | 600 | 400 | 400 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 3.86% | 5.62% | 1982 | 6847.5 | 52.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6847.5 | 1 | 0 | 6847.5 |  | 1
221075 | Inlet 017-R-176 | 250 | 3 |  | 2123 | 762 | 508 | 720 |  | 508 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NO | YES | 3.53% | 3.53% | 2015 | 63 | 14.53 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 63 | 1 | 0 | 63 |  | 1
3489600225 | HPSS 3489600225 | 250 | 3 |  | 3539 | 750 | 500 | 740 |  | 500 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NA | NA | 3.53% | NA | 2017 | 41 | 11.53 | No Action Needed | -- | 1 | 1 | 0 | 41 | 1 | 0 | 41 |  | 1
213962 | 4" La Conner H.P. Line | 151 | 3 |  | 1106 | 622 | 414 | 720 |  | 414 | X | X | VALID | 4.5 | 0.188 | 52000 | 0.6 | NO | YES | YES | 3.48% | 4.10% | 2015 | 316 | 20.1 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 316 | 1 | 0 | 316 |  | 1
178131 | 4" Sedro-Woolley H.P. Line | 100 | 3 |  | 877 | 375 | 250 | 720 |  | 250 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 3.42% | 2.71% | 2010 | 284 | 21.92 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 284 | 1 | 0 | 284 |  | 1
205109 | Inlet 017-R-172 | 105 | 3 |  | 1193 | 275 | 183 | 720 |  | 183 | X | X | VALID | 1.315 | 0.109 | 24000 | 0.6 | NO | YES | YES | 2.64% | 2.64% | 1985 | 24 | 32.64 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 24 | 1 | 0 | 24 |  | 1
193978 | Anacortes H.P. Distribution System (Inlet 017-R-170) | 105 | 3 |  | 499 | 300 | 200 | 720 |  | 200 | X | X | VALID | 4.5 | 0.237 | 42000 | 0.6 | NO | YES | YES | 2.37% | 6.31% | 2014 | 417.6 | 27.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 417.6 | 1 | 0 | 417.6 |  | 1
200583 | 4" Sedro-Woolley H.P. Line (Inlet 017-R-171) | 100 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 52000 | 0.6 | NO | YES | YES | 2.30% | 6.01% | 2013 | 35.8 | 27.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35.8 | 1 | 0 | 35.8 |  | 1
184809 | Inlet 017-R-161 | 151 | 3 |  | 2123 | 600 | 400 | 720 |  | 400 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 2.13% | NA | 2011 | 11 | 15.13 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 11 | 1 | 0 | 11 |  | 1
1951877956 | HPSS 1951877956 | 151 | 3 |  | 3539 | 760 | 506 | 740 |  | 506 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NA | NA | 2.13% | NA | 2017 | 30 | 10.13 | No Action Needed | -- | 1 | 1 | 0 | 30 | 1 | 0 | 30 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
G0022381 | 2" Gibralter Rd H.P. Line (017-V-094) | 250 | 3 |  | NA | NA | NA | UNKV |  | UNKV | X | X | UNVALID | NA | NA | NA | NA | YES | NA | NA | NA | NA | 1999 | 0 | 19 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 0 |  | 0 | 0
122 | Naval Air Station Service | 400 | 3 |  | 544 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 29.37% | 29.36% | 1972 | 67 | 90.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 67 |  | 0 | 0
150030 | HPSS 150030 (Texaco M&R) | 360 | 3 |  | 544 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 26.43% | 26.43% | 1992 | 174.7 | 78.93 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 174.7 |  | 0 | 0
16052-T | 6" Whidbey Island H.P. Line (017-V-007) | 400 | 3 |  | 544 | 700 | 466 | UNKV |  | 466 | X | NA | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 20.14% | 29.37% | 1969 | 68.1 | 87.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 68.1 | 0 |  | 0 | 0
G0071168 | 6" North Oak Harbor H.P. Line | 400 | 3 |  | 544 | 860 | 573 | UNKV |  | 544 | X | X | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 20.14% | 29.37% | 2003 | 282.6 | 66.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 282.6 |  | 0 | 0
GG002454 | 4" South Texas Rd H.P. Line | 500 | 3 |  | 1305 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 6.625 | 0.188 | 46000 | 1 | YES | NO | NO | 19.15% | 16.90% | 2002 | 634.7 | 53.65 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 634.7 |  | 0 | 0
161304 | 6" Mount Vernon H.P. Line | 250 | 3 |  | 499 | 750 | 500 | UNKV |  | 499 | X | X | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 18.35% | 18.35% | 2009 | 6926 | 56.35 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6926 |  | 0 | 0
184006 | 12" Anacortes H.P. Line | 500 | 3 |  | 1223 | 790 | 526 | UNKV |  | 526 | X | X | UNVALID | 12.75 | 0.375 | 52000 | 0.8 | YES | NO | YES | 16.35% | 16.35% | 2012 | 7517.2 | 48.85 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7517.2 |  | 0 | 0
44423 | 6" South Mount Vernon H.P. Line | 250 | 3 |  | 544 | 600 | 400 | UNKV |  | 400 | X | X | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 12.59% | 18.35% | 1993 | 25276.5 | 69.35 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25276.5 |  | 0 | 0
G0080804 | 017-R-148 | 360 | 3 |  | 933 | 650 | 433 | UNKV |  | 433 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 11.57% | 11.57% | 2006 | 139.7 | 42.07 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 139.7 |  | 0 | 0
700075 | HPSS 700075 | 400 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 10.05% | NA | 2004 | 12 | 40.55 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
647571 | Inlet 017-R-020 | 400 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 10.05% | NA | 1983 | 12 | 51.05 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
8540927401 | HPSS 8540927401 | 400 | 3 |  | 1214 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 9.88% | NA | 2013 | 52 | 30.88 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
301807 | HPSS 2526100597 | 500 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.68% | NA | 1978 | 183.2 | 49.18 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 183.2 |  | 0 | 0
1640 | HPSS 1640 | 500 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.68% | NA | 1983 | 8 | 45.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
140200 | HPSS 140200 | 500 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.68% | NA | 1992 | 4.1 | 41.18 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4.1 |  | 0 | 0
300422 | HPSS 300422 | 500 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.68% | NA | 1993 | 32 | 40.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 32 |  | 0 | 0
16002 | HPSS 16002 | 500 | 3 |  | 1549 | 790 | 526 | UNKV |  | 526 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.68% | NA | 1994 | 5 | 40.18 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
147010 | HPSS 147010 | 500 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.68% | NA | 1995 | 82.2 | 39.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 82.2 |  | 0 | 0
140044 | HPSS 140044 | 500 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 9.68% | NA | 2006 | 15 | 34.18 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
10030 | HPSS 10030 | 360 | 3 |  | 1193 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 9.05% | NA | 1963 | 1 | 59.55 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 1 | 0 |  | 0 | 0
3016795011 | HPSS 3016795011 | 360 | 3 |  | 1193 | 755 | 503 | UNKV |  | 503 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 9.05% | NA | 2014 | 20 | 29.55 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
35840 | 4" North Texas Rd H.P. Line | 250 | 3 |  | 499 | 375 | 250 | UNKV |  | 250 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 8.55% | 15.02% | 1974 | 1377.6 | 68.02 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1377.6 |  | 0 | 0
37486 | 4" South Anacortes H.P. Line | 250 | 3 |  | 877 | 375 | 250 | UNKV |  | 250 | X | X | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 8.55% | 6.78% | 1990 | 10400 | 56.05 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10400 |  | 0 | 0
47079 | Inlet 017-R-108 | 250 | 3 |  | 877 | 675 | 450 | UNKV |  | 450 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | NO | YES | 8.55% | 6.78% | 1995 | 55.1 | 34.55 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
46863 | Inlet 017-R-098 | 250 | 3 |  | 877 | 600 | 400 | UNKV |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | NO | YES | 8.55% | 6.78% | 1995 | 32.1 | 34.55 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 32.1 |  | 0 | 0
620032 | HPSS 620032 | 400 | 3 |  | 1456 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.315 | 0.133 | 24000 | 0.6 | YES | NA | NA | 8.24% | NA | 2006 | 20.7 | 32.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.7 |  | 0 | 0
45637 | Inlet 017-R-106 | 360 | 3 |  | 1361 | 750 | 500 | UNKV |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NA | NA | 7.93% | NA | 1994 | 78.3 | 34.43 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 78.3 |  | 0 | 0
53268 | Inlet 017-R-045 | 360 | 3 |  | 1361 | 750 | 500 | UNKV |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NO | YES | 7.93% | 7.93% | 1997 | 23.9 | 32.93 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.9 |  | 0 | 0
640115 | HPSS 640115 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2003 | 2.1 | 33.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2.1 |  | 0 | 0
626902 | HPSS 32400704 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1972 | 10 | 49.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
646100 | HPSS 646100 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1977 | 16.3 | 46.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.3 |  | 0 | 0
626200 | HPSS 626200 | 400 | 3 |  | 1549 | 850 | 566 | UNKV |  | 566 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1978 | 25 | 46.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
626785 | HPSS 626785 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1981 | 45.6 | 44.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45.6 |  | 0 | 0
626850 | HPSS 626850 | 400 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1984 | 79 | 43.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 79 |  | 0 | 0
629060 | HPSS 629060 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1985 | 20 | 42.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
646110 | HPSS 646110 | 400 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1985 | 52.2 | 42.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52.2 |  | 0 | 0
646501 | HPSS 646501 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1985 | 19 | 42.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
626912 | HPSS 626912 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1986 | 24 | 42.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24 |  | 0 | 0
626624 | HPSS 626624 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1987 | 91.1 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 91.1 |  | 0 | 0
626855 | HPSS 626855 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1987 | 66.1 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 66.1 |  | 0 | 0
646655 | HPSS 646655 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1987 | 64 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 64 |  | 0 | 0
701220 | HPSS 701220 | 400 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1987 | 5 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
626800 | HPSS 626800 | 400 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1988 | 45 | 41.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
626917 | HPSS 626917 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1988 | 48.7 | 41.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48.7 |  | 0 | 0
646659 | HPSS 646659 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1988 | 84.4 | 41.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 84.4 |  | 0 | 0
626901 | HPSS 626901 | 400 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1989 | 17 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
643470 | HPSS 643470 | 400 | 3 |  | 1549 | 675 | 450 | UNKV |  | 450 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1989 | 107 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 107 |  | 0 | 0
647512 | HPSS 647512 | 400 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1989 | 41.4 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41.4 |  | 0 | 0
702010 | HPSS 702010 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1989 | 61.9 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 61.9 |  | 0 | 0
628078 | HPSS 628078 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1990 | 135 | 41.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 135 |  | 0 | 0
629091 | HPSS 629091 | 400 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1990 | 74.9 | 40.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 74.9 |  | 0 | 0
620025 | HPSS 620025 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 19.6 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19.6 |  | 0 | 0
620031 | HPSS 620031 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 77.8 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77.8 |  | 0 | 0
620038 | HPSS 620038 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 58.6 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58.6 |  | 0 | 0
626625 | HPSS 626625 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 108.3 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 108.3 |  | 0 | 0
628077 | HPSS 628077 | 400 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1991 | 327 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 327 |  | 0 | 0
629031 | HPSS 629031 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 105.1 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 105.1 |  | 0 | 0
640014 | HPSS 641901 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 81 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 81 |  | 0 | 0
700001 | HPSS 700001 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 307 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 307 |  | 0 | 0
700002 | HPSS 700002 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 15 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
700003 | HPSS 700003 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1991 | 378.7 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 378.7 |  | 0 | 0
701101 | HPSS 701101 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 77.1 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77.1 |  | 0 | 0
701275 | HPSS 701275 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 12 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
620139 | HPSS 620139 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1992 | 48.2 | 39.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48.2 |  | 0 | 0
621364 | HPSS 621364 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1992 | 10.1 | 39.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10.1 |  | 0 | 0
621366 | HPSS 621366 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1992 | 38 | 39.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
629069 | HPSS 629069 | 400 | 3 |  | 1549 | 755 | 503 | UNKV |  | 503 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1992 | 111.8 | 40.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 111.8 |  | 0 | 0
620005 | HPSS 620005 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 21 | 38.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
629006 | HPSS 629006 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 15 | 38.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
700006 | HPSS 700006 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 12 | 38.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
4963400980 | HPSS 4963400980 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 30 | 38.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
620621 | HPSS 620621 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 20 | 38.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
621011 | HPSS 621011 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 45 | 38.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
621032 | HPSS 621032 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 42.8 | 38.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.8 |  | 0 | 0
621036 | HPSS 621036 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 20.9 | 38.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.9 |  | 0 | 0
624053 | HPSS 624053 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 57.8 | 38.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.8 |  | 0 | 0
620003 | HPSS 620003 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 10 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
620006 | HPSS 620006 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 15.1 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15.1 |  | 0 | 0
620007 | HPSS 620007 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 15 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
620012 | HPSS 620012 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 18 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
620902 | HPSS 620902 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 14.9 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14.9 |  | 0 | 0
622092 | HPSS 622092 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1995 | 43 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
622203 | HPSS 622203 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 52 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
624055 | HPSS 624055 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 24 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24 |  | 0 | 0
640048 | HPSS 640048 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1995 | 18.9 | 37.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18.9 |  | 0 | 0
627002 | HPSS 627002 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 45.1 | 37.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45.1 |  | 0 | 0
700051 | HPSS 700051 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 50 | 37.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
700057 | HPSS 700057 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 18 | 37.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
620903 | HPSS 620903 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1997 | 35.5 | 36.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35.5 |  | 0 | 0
626551 | HPSS 626551 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1997 | 38 | 36.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
626626 | HPSS 626626 | 400 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1997 | 30 | 36.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
604105 | HPSS 604105 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1998 | 34.7 | 36.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.7 |  | 0 | 0
602226 | HPSS 602226 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1999 | 14 | 35.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
602243 | HPSS 602243 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1999 | 26 | 35.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26 |  | 0 | 0
700065 | HPSS 700065 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1999 | 12.9 | 35.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12.9 |  | 0 | 0
700082 | HPSS 700082 | 400 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1999 | 85.2 | 35.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 85.2 |  | 0 | 0
600920 | HPSS 600920 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2001 | 47.9 | 34.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47.9 |  | 0 | 0
602376 | HPSS 602376 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2005 | 15 | 32.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
700147 | HPSS 700147 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2005 | 13 | 32.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
7973400069 | HPSS 7973400069 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2006 | 17.1 | 32.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17.1 |  | 0 | 0
640115 | HPSS 640115 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2007 | 42 | 31.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
8370445997 | HPSS 8370445997 | 360 | 3 |  | 1456 | 796 | 530 | UNKV |  | 530 | X | Service | UNVALID | 1.315 | 0.133 | 24000 | 0.6 | YES | NA | NA | 7.42% | NA | 2015 | 29 | 27.42 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29 |  | 0 | 0
4828142892 | HPSS 4828142892 | 500 | 3 |  | 2123 | 780 | 520 | UNKV |  | 520 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 7.06% | NA | 2016 | 31 | 22.56 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31 |  | 0 | 0
13170 | Service Stub | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1992 | 1 | 38.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1 |  | 0 | 0
10876 | HPSS 10876 | 360 | 3 |  | 1549 | 1000 | 666 | UNKV |  | 666 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1974 | 1 | 47.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1 |  | 0 | 0
10021 | HPSS 10021 | 360 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1978 | 3 | 45.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 3 |  | 0 | 0
420800 | HPSS 420800 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1980 | 7.1 | 44.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7.1 |  | 0 | 0
10018 | HPSS 9420000099 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1982 | 6 | 43.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
10023 | HPSS 10023 | 360 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1984 | 8 | 42.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
10877 | HPSS 10877 | 360 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1985 | 19.9 | 41.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19.9 |  | 0 | 0
420810 | HPSS 420810 | 360 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1985 | 31.6 | 41.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31.6 |  | 0 | 0
10026 | HPSS 10026 | 360 | 3 |  | 1549 | 1000 | 666 | UNKV |  | 666 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1986 | 45 | 41.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
210269 | HPSS 210269 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1989 | 50 | 39.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
420804 | HPSS 420804 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1989 | 133 | 40.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 133 |  | 0 | 0
10043 | HPSS 10043 | 360 | 3 |  | 1549 | 630 | 420 | UNKV |  | 420 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1990 | 51 | 39.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
300014 | HPSS 300014 | 360 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1990 | 167 | 40.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 167 |  | 0 | 0
11003 | HPSS 11003 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 6.97% | 6.97% | 1991 | 43.4 | 38.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43.4 |  | 0 | 0
14020 | HPSS 14020 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1992 | 19.3 | 38.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19.3 |  | 0 | 0
10908 | HPSS 10908 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1993 | 25 | 37.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
300895 | HPSS 300895 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 6.97% | 6.97% | 1993 | 15.9 | 37.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15.9 |  | 0 | 0
210482 | HPSS 210482 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1994 | 20 | 37.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
300264 | HPSS 300264 | 360 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1994 | 114.9 | 38.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 114.9 |  | 0 | 0
420210 | HPSS 420210 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 6.97% | 6.97% | 1994 | 214.6 | 38.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 214.6 |  | 0 | 0
148200 | HPSS 148200 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1996 | 18.1 | 36.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18.1 |  | 0 | 0
29200 | HPSS 29200 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1997 | 19 | 35.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
147100 | HPSS 147100 | 360 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1997 | 12 | 35.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
300924 | HPSS 300924 | 360 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1997 | 24.9 | 35.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24.9 |  | 0 | 0
18300 | HPSS 18300 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 1998 | 15 | 35.47 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
420220 | HPSS 420220 | 360 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 2003 | 15.6 | 32.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15.6 |  | 0 | 0
10946 | HPSS 10946 | 360 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 2005 | 12.3 | 31.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12.3 |  | 0 | 0
144055 | HPSS 144055 | 360 | 3 |  | 1549 | 830 | 553 | UNKV |  | 553 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.97% | NA | 2005 | 3 | 31.97 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 3 |  | 0 | 0
555660 | HPSS 555660 | 250 | 3 |  | 1193 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 6.28% | 6.28% | 1989 | 4.9 | 39.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4.9 |  | 0 | 0
18035 | HPSS 18035 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2009 | 13 | 29.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
7246184565 | HPSS 7246184565 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2012 | 51 | 27.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
6823202244 | HPSS 6823202244 | 250 | 3 |  | 1193 | 790 | 526 | UNKV |  | 526 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2014 | 20 | 26.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
6898886189 | HPSS 6898886189 | 250 | 3 |  | 1193 | 790 | 526 | UNKV |  | 526 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2014 | 8 | 26.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
7007685992 | HPSS 7007685992 | 250 | 3 |  | 1193 | 790 | 526 | UNKV |  | 526 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NO | YES | 6.28% | 3.53% | 2015 | 67 | 26.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 67 |  | 0 | 0
380170 | HPSS 380170 | 249 | 3 |  | 1214 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | YES | YES | 6.15% | 6.15% | 1993 | 167 | 38.15 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 167 |  | 0 | 0
570252 | HPSS 570252 | 250 | 3 |  | 1237 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.315 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.06% | NA | 1995 | 46 | 36.06 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
570282 | HPSS 570282 | 250 | 3 |  | 1237 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.113 | 24000 | 0.6 | YES | NA | NA | 6.06% | NA | 2005 | 21.1 | 31.06 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21.1 |  | 0 | 0
602278 | HPSS 602278 | 400 | 3 |  | 2260 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 5.31% | NA | 1999 | 24.1 | 29.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24.1 |  | 0 | 0
700068 | HPSS 700068 | 400 | 3 |  | 2260 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 5.31% | NA | 1999 | 22.4 | 29.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22.4 |  | 0 | 0
894 | HPSS 894 | 400 | 3 |  | 2260 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 5.31% | NA | 2000 | 42.3 | 28.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.3 |  | 0 | 0
600954 | HPSS 600954 | 400 | 3 |  | 2260 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 5.31% | NA | 2000 | 17 | 28.81 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
224186 | Anacortes H.P. Distribution System | 105 | 3 |  | 499 | 300 | 200 | UNKV |  | 200 | X | X | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 5.29% | 7.71% | 1995 | 2399.2 | 45.21 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2399.2 |  | 0 | 0
24C9676 | 4" La Conner H.P. Line | 151 | 3 |  | 499 | 660 | 440 | UNKV |  | 440 | X | NA | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 5.16% | 9.07% | 1965 | 21225.3 | 72.57 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 21225.3 | 0 |  | 0 | 0
1450 | HPSS 150114 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1980 | 138.5 | 38.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 138.5 |  | 0 | 0
497695 | HPSS 497695 | 250 | 4 |  | 1239 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 55.1 | 38.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
497497 | HPSS 497497 | 250 | 4 |  | 1239 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 84.5 | 36.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 84.5 |  | 0 | 0
555856 | HPSS 555856 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 40.3 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.3 |  | 0 | 0
497720 | HPSS 497720 | 250 | 4 |  | 1239 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 49.2 | 35.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.2 |  | 0 | 0
497450 | HPSS 497450 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 65.7 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 65.7 |  | 0 | 0
497500 | HPSS 497500 | 250 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 95.9 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 95.9 |  | 0 | 0
560005 | HPSS 560005 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 16 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
560108 | HPSS 560108 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 74.6 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 74.6 |  | 0 | 0
490017 | HPSS 490017 | 250 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 41.1 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41.1 |  | 0 | 0
490023 | HPSS 490023 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 56.3 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56.3 |  | 0 | 0
560700 | HPSS 560700 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1991 | 114.4 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 114.4 |  | 0 | 0
492002 | HPSS 492002 | 250 | 4 |  | 1239 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1992 | 53.4 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 53.4 |  | 0 | 0
490079 | HPSS 490100 | 250 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 55.1 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55.1 |  | 0 | 0
490211 | HPSS 490211 | 250 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 9 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
560431 | HPSS 560431 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 67.2 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 67.2 |  | 0 | 0
560447 | HPSS 560447 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 26 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26 |  | 0 | 0
560451 | HPSS 560451 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 49.1 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.1 |  | 0 | 0
560473 | HPSS 560473 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 11 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
560475 | HPSS 560475 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 24.9 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 24.9 |  | 0 | 0
570266 | HPSS 570266 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 31 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31 |  | 0 | 0
570272 | HPSS 570272 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 70 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 70 |  | 0 | 0
570300 | HPSS 570300 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 58 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
490321 | HPSS 490321 | 250 | 4 |  | 1239 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 12.8 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12.8 |  | 0 | 0
570287 | HPSS 570287 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 19 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
490294 | HPSS 490294 | 250 | 4 |  | 1239 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 122.7 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 122.7 |  | 0 | 0
560581 | HPSS 560581 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 5.4 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5.4 |  | 0 | 0
570297 | HPSS 570297 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 46 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
560682 | HPSS 560682 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 10 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
570353 | HPSS 570353 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 44 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
570354 | HPSS 570354 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 13.2 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13.2 |  | 0 | 0
570355 | HPSS 570355 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 44 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
570382 | HPSS 570382 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 50 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
570551 | HPSS 570551 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 21 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
560477 | HPSS 560477 | 250 | 3 |  | 1549 | 748 | 498 | UNKV |  | 498 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 23.9 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.9 |  | 0 | 0
560491 | HPSS 560491 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 23.7 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.7 |  | 0 | 0
570363 | HPSS 570363 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2005 | 63.1 | 24.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 63.1 |  | 0 | 0
561092 | HPSS 561092 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2008 | 33.5 | 23.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 33.5 |  | 0 | 0
381049 | HPSS 381049 | 249 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.82% | NA | 1998 | 53 | 28.32 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 53 |  | 0 | 0
381320 | HPSS 381320 | 249 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.82% | 4.82% | 1998 | 44 | 28.32 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
56519 | Inlet 017-R-125 | 360 | 3 |  | 2260 | 800 | 533 | UNKV |  | 533 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 4.78% | NA | 1989 | 246.7 | 29.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 246.7 |  | 0 | 0
4626525386 | HPSS 4626525386 | 151 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 3.80% | NA | 2012 | 10 | 20.3 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
17254 | Anacortes H.P. Distribution System | 105 | 3 |  | 492 | 370 | 264 | UNKV |  | 264 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | YES | YES | YES | 3.59% | 6.39% | 1970 | 1843 | 57.39 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 1843 | 0 |  | 0 | 0
290040 | HPSS 290040 | 175 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1991 | 83.6 | 30.39 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 83.6 |  | 0 | 0
2295 | HPSS 2295 | 175 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1992 | 54 | 29.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
290109 | HPSS 2934100003 | 175 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.39% | 3.39% | 1994 | 88 | 28.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 88 |  | 0 | 0
570404 | HPSS 570404 | 250 | 3 |  | 2260 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2000 | 60 | 21.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60 |  | 0 | 0
126016 | HPSS 126016 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | YES | YES | 3.32% | 4.84% | 2001 | 61.7 | 26.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 61.7 |  | 0 | 0
420002 | HPSS 420002 | 151 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.92% | 2.92% | 1975 | 35 | 37.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
420001 | HPSS 420001 | 151 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1979 | 42 | 35.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
420017 | HPSS 420017 | 151 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1980 | 57 | 35.42 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57 |  | 0 | 0
420020 | HPSS 420020 | 151 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1985 | 36 | 32.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
420022 | HPSS 420022 | 151 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1986 | 58 | 32.42 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
420027 | HPSS 420027 | 151 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.92% | 2.92% | 1988 | 97.9 | 31.42 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 97.9 |  | 0 | 0
420400 | HPSS 420400 | 151 | 3 |  | 1549 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.92% | 2.92% | 1990 | 105.7 | 31.42 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 105.7 |  | 0 | 0
420032 | HPSS 420032 | 151 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.92% | 2.92% | 1991 | 124.6 | 30.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 124.6 |  | 0 | 0
420104 | HPSS 420104 | 151 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.92% | 2.92% | 1991 | 267 | 30.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 267 |  | 0 | 0
420105 | HPSS 420105 | 151 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.92% | 2.92% | 1991 | 172.4 | 30.92 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 172.4 |  | 0 | 0
420532 | HPSS 420532 | 151 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.92% | NA | 1998 | 39 | 26.42 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39 |  | 0 | 0
1780000537 | HPSS 1780000537 | 105 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 2.64% | NA | 2013 | 21.5 | 18.64 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21.5 |  | 0 | 0
10980 | HPSS 10980 | 105 | 3 |  | 1549 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1958 | 77.7 | 52.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 77.7 | 0 |  | 0 | 0
10817 | HPSS 7380000506 | 105 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 2.03% | 2.03% | 1965 | 17.5 | 45.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 17.5 | 0 |  | 0 | 0
10856 | HPSS 10856 | 105 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1978 | 16.6 | 35.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.6 |  | 0 | 0
10593 | HPSS 10593 | 105 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1979 | 41 | 35.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41 |  | 0 | 0
10828 | HPSS 10828 | 105 | 3 |  | 1549 | 350 | 233 | UNKV |  | 233 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1986 | 17.8 | 31.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17.8 |  | 0 | 0
10829 | HPSS 10829 | 105 | 3 |  | 1549 | 350 | 233 | UNKV |  | 233 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1986 | 19 | 31.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
10809 | HPSS 10809 | 105 | 3 |  | 1549 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1987 | 16 | 31.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
10842 | HPSS 10842 | 105 | 3 |  | 1549 | 300 | 200 | UNKV |  | 200 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1989 | 51.7 | 30.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51.7 |  | 0 | 0
10996 | HPSS 10996 | 105 | 3 |  | 1549 | 160 | 106 | UNKV |  | 106 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1990 | 46.2 | 29.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46.2 |  | 0 | 0
16001 | HPSS 16001 | 105 | 3 |  | 1549 | 263 | 175 | UNKV |  | 175 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1991 | 70.1 | 29.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 70.1 |  | 0 | 0
10991 | HPSS 10991 | 105 | 3 |  | 1549 | 263 | 175 | UNKV |  | 175 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1992 | 80 | 28.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 80 |  | 0 | 0
24000 | HPSS 24000 | 105 | 3 |  | 1549 | 265 | 176 | UNKV |  | 176 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 1992 | 147.5 | 29.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 147.5 |  | 0 | 0
11077 | HPSS 401000792 | 105 | 3 |  | 1549 | 250 | 166 | UNKV |  | 166 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.03% | NA | 2013 | 34.8 | 18.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 34.8 |  | 0 | 0
401000792 | HPSS 401000792 | 105 | 3 |  | 3539 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 1 | YES | NO | NO | 1.48% | 1.48% | 2013 | 0 | 11.48 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 0 |  | 0 | 0
42924 | 6" South Mount Vernon H.P. Line | 250 | 3 |  | 544 | 600 | 400 | 250 |  | 250 | X |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 18.35% | 1993 | 5746.1 | 64.35 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 5746.1 |  | 0 | 0
39617 | Inlet 017-R-100 | 500 | 3 |  | 1193 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 11.02% | 12.57% | 1992 | 74.8 | 49.07 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 74.8 |  | 0 | 0
198411 | 017-V-216 | 500 | 3 |  | 1361 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 11.02% | 7.78% | 2012 | 44.4 | 33.52 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 44.4 |  | 0 | 0
33831 | 6" North Oak Harbor H.P. Line (Inlet 017-R-076) | 400 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1986 | 99.2 | 39.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 99.2 |  | 0 | 0
G0083869 | Inlet 017-R-175 | 400 | 3 |  | 1361 | 780 | 520 | 720 |  | 520 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 2009 | 77.1 | 27.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 77.1 |  | 0 | 0
49815 | Inlet 017-R-114 | 400 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1996 | 72.3 | 34.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 72.3 |  | 0 | 0
50252 | Inlet 017-R-117 | 400 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1997 | 51 | 33.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 51 |  | 0 | 0
58345 | Inlet 017-R-131 | 400 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 2000 | 59.2 | 32.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 59.2 |  | 0 | 0
G0073225 | Inlet 017-R-145 | 400 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 2004 | 44.5 | 30.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 44.5 |  | 0 | 0
G0083505 | Inlet 017-R-153 | 400 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 2008 | 5.3 | 28.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 5.3 |  | 0 | 0
55557 | Inlet 017-R-121 | 250 | 3 |  | 933 | 700 | 466 | NA |  | 466 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1998 | 324.5 | 37.53 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 324.5 |  | 0 | 0
42178 | Inlet 017-R-095 | 249 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.00% | NA | 1992 | 21 | 39.5 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 21 |  | 0 | 0
41521 | 8" March Point H.P. Line (Inlet 017-R-132) | 360 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 7.93% | 7.93% | 1992 | 539.7 | 40.43 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 539.7 |  | 0 | 0
45940 | Inlet 017-R-105 | 360 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 7.93% | 7.93% | 1994 | 156 | 35.43 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 156 |  | 0 | 0
47084 | Inlet 017-R-107 | 360 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 7.93% | NA | 1994 | 67.2 | 34.43 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 67.2 |  | 0 | 0
48868 | Inlet 017-R-110 | 360 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 7.93% | 7.93% | 1995 | 26.9 | 33.93 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 26.9 |  | 0 | 0
GG008936 | 4" South Anacortes H.P. Line | 250 | 3 |  | 1052 | 792 | 528 | 720 |  | 528 | X |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 7.12% | 6.78% | 2005 | 60.9 | 32.12 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 60.9 |  | 0 | 0
36159 | 4" North Texas Rd H.P. Line | 250 | 3 |  | 499 | 375 | 250 | 1440 |  | 250 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 15.02% | 1988 | 14.2 | 53.52 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.2 |  | 0 | 0
49967 | Inlet 017-R-115 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1995 | 20 | 31.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 20 |  | 0 | 0
49702 | Inlet 017-R-113 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1996 | 25.2 | 31.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 25.2 |  | 0 | 0
42185 | Inlet 017-R-094 | 249 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.49% | NA | 1982 | 14.7 | 37.99 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 14.7 |  | 0 | 0
44844 | Inlet 017-R-102 | 249 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.49% | 5.49% | 1994 | 22.1 | 31.99 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 22.1 |  | 0 | 0
50290 | Inlet 017-R-116 | 249 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.49% | 5.49% | 1996 | 26.4 | 30.99 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 26.4 |  | 0 | 0
28304 | Inlet 017-R-067 | 400 | 3 |  | 2260 | 750 | 500 | 1200 |  | 500 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 5.31% | NA | 1980 | 15.6 | 38.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 15.6 |  | 0 | 0
53019 | Anacortes H.P. Distribution System | 105 | 3 |  | 811 | 275 | 183 | NA |  | 183 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 5.18% | 4.02% | 1997 | 26.8 | 30.18 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 26.8 |  | 0 | 0
30082 | Inlet 017-R-077 | 175 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.86% | 3.86% | 1982 | 886.7 | 36.36 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 886.7 |  | 0 | 0
52559 | Inlet 017-R-118 | 151 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.33% | 3.33% | 1997 | 21 | 23.33 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 21 |  | 0 | 0
26117 | Inlet 017-R-042 | 105 | 3 |  | 1361 | 600 | 400 | NA |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 2.31% | 2.31% | 1979 | 26 | 31.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 26 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
32375 | Inlet 017-R-023 | 105 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 2.31% | 2.31% | 1985 | 41.6 | 28.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 41.6 |  | 0 | 0
33004 | Inlet 017-R-026 | 105 | 3 |  | 1361 | 675 | 450 | 1440 |  | 450 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 2.31% | 2.31% | 1986 | 20.4 | 27.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 20.4 |  | 0 | 0
34257 | Inlet 017-R-079 | 105 | 3 |  | 1193 | 250 | 166 | 1440 |  | 166 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 2.31% | 2.64% | 1987 | 78.2 | 31.64 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 78.2 |  | 0 | 0
41293 | Inlet 017-R-093 | 105 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 2.31% | NA | 1991 | 17.8 | 25.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 17.8 |  | 0 | 0
45845 | Inlet 017-R-104 | 105 | 3 |  | 1361 | 265 | 176 | 1440 |  | 176 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 2.31% | 2.31% | 1994 | 7 | 23.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 7 |  | 0 | 0
51883 | Inlet 017-R-043 | 105 | 3 |  | 1361 | 275 | 183 | 1440 |  | 183 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 2.31% | 2.31% | 1997 | 21.1 | 22.31 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 21.1 |  | 0 | 0
60209 | Fredonia Compressor Station | 500 | 3 |  | 375 | 800 | 533 | UNKV |  | 375 |  | X | UNVALID | 16 | 0.25 | 35000 | 1 | YES | YES | NO | 59.56% | 66.67% | 2001 | 483.1 | 117.67 | In-Situ Test | 2018-2019 | 1 | 1 | 0 | 483.1 |  | 0 | 0
4086545446 | Inlet M&R 191484 | 500 | 3 |  | 758 | 780 | 520 | UNKV |  | 520 | X | Service | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | YES | YES | YES | 14.25% | 19.78% | 2012 | 62 | 46.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 62 |  | 0 | 0
45730 | 16" March Point Transmission Line | 500 | 3 |  | 437 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 16 | 0.25 | 35000 | 0.8 | NO | NA | NA | 45.71% | NA | 1993 | 3 | 137.71 | Pressure Test/Replace | 2018-2019 | 1 | 1 | 0 | 3 |  | 0 | 0
16049 | 017-O-003 | 960 | 3 |  | 1183 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.28 | 52000 | 0.8 | YES | NO | YES | 21.84% | 32.45% | 1970 | 120.7 | 126.95 | Pressure Test/Replace | 2018-2019 | 1 | 0 | 120.7 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
WWL1-1 | 8" Walla Walla H.P. Line | 150 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 14.34% | NA | 1956 | 5345 | 108.34 | 116 Segment, Pressure Test | 2020 | 1 | 0 | 5345 | 0 |  | 0 | 0
WWL2-1 | 3" College Place H.P. Line | 150 | 3 |  | 641 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 7.01% | 7.01% | 1956 | 2660.6 | 92.05 | 116 Segment, Retire | 2022 | 1 | 0 | 2660.6 | 0 |  | 0 | 0
3503801004 | Service Stub | 150 | 3 |  | 1193 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | YES | YES | 3.77% | 3.77% | 2010 | 25 | 22.27 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 25 |  | 0 | 0
UNKV | O26-O-001 to Williams | 150 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 14.34% | NA | 1956 | 0 | 98.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 0 | 0 |  | 0 | 0
MM000188 | 026-V-030 | 150 | 3 |  | 908 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 4.07% | 6.60% | 2002 | 17 | 29.1 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 17 | 1 | 0 | 17 |  | 1
MM000189 | 026-V-031 | 150 | 3 |  | 908 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.322 | 46000 | 0.8 | NO | NO | YES | 4.37% | 6.60% | 2002 | 20.7 | 29.1 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20.7 | 1 | 0 | 20.7 |  | 1
MM000190 | 026-O-001 | 150 | 3 |  | 418 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 14.34% | 8.37% | 2002 | 62.2 | 45.84 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 62.2 | 1 | 0 | 62.2 |  | 1
212245 | 6" College Place H.P. Line | 150 | 3 |  | 418 | 630 | 420 | 720 |  | 418 | X | X | VALID | 6.625 | 0.188 | 52000 | 0.8 | NO | YES | YES | 5.08% | 14.34% | 2015 | 3966.9 | 46.84 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3966.9 | 1 | 0 | 3966.9 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
WenL1-1,2 | 6" & 8" Moses Lake Transmission Line | 250 | 3 |  | 418 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 23.89% | 23.89% | 1957 | 16970.9 | 134.39 | 116 Segment, Replace | 2018 | 1 | 0 | 16970.9 | 0 |  | 0 | 0
WenL1-1,2 | 6" & 8" Moses Lake Transmission Line | 250 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 23.89% | NA | 1957 | 102.6 | 120.39 | 116 Segment, Replace | 2018 | 1 | 0 | 102.6 | 0 |  | 0 | 0
59C7038 | 4" Othello Transmission Line | 400 | 3 |  | 626 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 25000 | 0.6 | YES | YES | YES | 19.15% | 12.85% | 1963 | 62566.8 | 121.15 | 116 Segment, Replace | 2019 | 1 | 0 | 62566.8 | 0 |  | 0 | 0
14455 | 4" South Moses Lake H.P. Line | 250 | 3 |  | 544 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 18.35% | 1968 | 3006.3 | 97.85 | 116 Segment, Pressure Test | 2017 | 1 | 0 | 3006.3 | 0 |  | 0 | 0
2912 | 6" Wenatchee H.P. Line | 225 | 3 |  | 544 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 16.52% | 16.52% | 1973 | 32219.6 | 102.52 | 116 Segment, Pressure Test | 2020 | 1 | 1 | 0 | 32219.6 |  | 0 | 0
WenL2-2 | 2" Wheeler H.P. Line | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1962 | 3673.8 | 87.03 | 116 Segment, Replace | 2022 | 1 | 0 | 3673.8 | 0 |  | 0 | 0
58C5745 | 2" Wheeler H.P. Line (Inlet 029-R-007) | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1962 | 210 | 80.53 | 116 Segment, Replace | 2022 | 1 | 0 | 210 | 0 |  | 0 | 0
18998 | 4" Othello Transmission Line | 400 | 3 |  | 499 | 531 | 354 | UNKV |  | 354 |  |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 20.14% | 24.04% | 1971 | 71.3 | 81.04 | 116 Segment, Replace | 2019 | 1 | 1 | 0 | 71.3 |  | 0 | 0
29378 | 6" & 8" Moses Lake Transmission Line | 250 | 3 |  | 610 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 16.38% | 9.57% | 1981 | 28.9 | 74.38 | 116 Segment, Replace | 2018 | 1 | 1 | 0 | 28.9 |  | 0 | 0
60390 | 6" & 8" Moses Lake Transmission Line (4" Main) | 250 | 3 |  | 499 | 375 | 250 | UNKV |  | 250 | X | X | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 15.02% | 15.02% | 1981 | 2031.2 | 64.52 | 116 Segment, Most Stringent Criteria | 2016 | 1 | 1 | 0 | 2031.2 |  | 0 | 0
3750010 | HPSS 3750010 | 400 | 3 |  | 1214 | 30 | 21 | UNKV |  | 21 |  |  | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 9.88% | NA | 1969 | 20 | 59.38 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 20 | 0 |  | 0 | 0
3660039 | HPSS 3660039 | 400 | 3 |  | 1549 | 50 | 35 | UNKV |  | 35 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1967 | 3 | 59.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 3 | 0 |  | 0 | 0
3764650 | HPSS 3764650 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 46 | 46.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 46 | 0 |  | 0 | 0
3400110 | Service to 3132 Road O NE | 100 | 3 |  | 933 | 125 | 83 | NA |  | 83 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 3.21% | 3.21% | 2008 | 57 | 22.71 | Addressed w/ 116 Segment | 2022 | 1 | 1 | 0 | 57 |  | 0 | 0
5791140 | HPSS 5791140 | 225 | 3 |  | 1549 | 90 | 64 | UNKV |  | 64 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1966 | 8 | 47.86 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 8 | 0 |  | 0 | 0
3260178 | Service Stub | 250 | 3 |  | 1549 | 118 | 78 | UNKV |  | 78 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1968 | 12 | 46.34 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 12 | 0 |  | 0 | 0
3761595 | HPSS 3761595 | 250 | 3 |  | 1549 | 100 | 71 | UNKV |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1968 | 17 | 46.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 17 | 0 |  | 0 | 0
3764575 | Service Stub | 250 | 3 |  | 1549 | 30 | 21 | UNKV |  | 21 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1969 | 10 | 45.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 10 | 0 |  | 0 | 0
5791420 | HPSS 5791420 | 225 | 3 |  | 1549 | 90 | 64 | UNKV |  | 64 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1969 | 9 | 44.86 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 9 | 0 |  | 0 | 0
14582 | Inlet 029-R-009 | 400 | 3 |  | 1361 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 1968 | 18 | 55.31 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 18 | 0 |  | 0 | 0
3260160 | HPSS 3260160 | 250 | 3 |  | 1193 | 225 | 150 | UNKV |  | 150 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1971 | 21.3 | 53.28 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 21.3 |  | 0 | 0
3660042 | HPSS 3660042 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1988 | 14 | 46.24 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 14 |  | 0 | 0
3260172 | HPSS 3260172 | 250 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1975 | 71 | 51.28 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 71 |  | 0 | 0
2566454439 | HPSS 2566454439 | 400 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 10.05% | NA | 2015 | 60 | 40.05 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 60 |  | 0 | 0
3400136 | HPSS 3400136 | 250 | 3 |  | 933 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1996 | 89 | 42.53 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 89 |  | 0 | 0
3260170 | HPSS 3260170 | 250 | 3 |  | 1193 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1982 | 18.3 | 47.78 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 18.3 |  | 0 | 0
3764580 | HPSS 3764580 | 250 | 3 |  | 1549 | 170 | 121 | UNKV |  | 121 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1970 | 7 | 44.34 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 7 | 0 |  | 0 | 0
3660002 | HPSS 3660002 | 400 | 3 |  | 1549 | 90 | 60 | UNKV |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2000 | 26.9 | 40.24 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 26.9 |  | 0 | 0
5850330 | Service Stub | 225 | 3 |  | 933 | 90 | 64 | UNKV |  | 64 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 7.23% | NA | 1997 | 60.2 | 41.23 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 60.2 |  | 0 | 0
3740170 | Inlet M&R 37072 | 100 | 3 |  | 499 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 6.01% | 6.01% | 1986 | 15 | 45.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
5790975 | HPSS 5790975 | 225 | 3 |  | 1549 | 115 | 82 | UNKV |  | 82 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1970 | 44.8 | 43.86 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 44.8 | 0 |  | 0 | 0
3400475 | HPSS 3400475 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1976 | 29.7 | 40.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 29.7 |  | 0 | 0
5790225 | HPSS 5790225 | 225 | 3 |  | 1549 | 110 | 73 | UNKV |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1972 | 186.3 | 42.86 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 186.3 |  | 0 | 0
3260171 | HPSS 3260171 | 250 | 3 |  | 1549 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 16.5 | 39.34 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 16.5 |  | 0 | 0
3260150 | HPSS 3260150 | 250 | 3 |  | 1549 | 225 | 150 | UNKV |  | 150 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1983 | 31.7 | 36.84 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 31.7 |  | 0 | 0
3764565 | HPSS 3764565 | 250 | 3 |  | 1549 | 250 | 166 | UNKV |  | 166 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 49 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
9769720060 | HPSS 9769720060 | 250 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 18 | 36.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
22118 | 029-R-008, M&R 37072 | 400 | 3 |  | 1361 | 98 | 65 | 1440 |  | 65 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1973 | 9 | 50.81 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 9 |  | 0 | 0
3764600 | HPSS 3764600 | 250 | 3 |  | 1549 | 100 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 16 | 31.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
3370114 | HPSS 3370114 | 250 | 3 |  | 1549 | 98 | 65 | UNKV |  | 65 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 5.6 | 26.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 5.6 |  | 0 | 0
3764579 | HPSS 3764579 | 250 | 3 |  | 1549 | 90 | 1 | UNKV |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 3 | 25.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 3 |  | 0 | 0
199470 | Inlet 029-R-062 | 400 | 3 |  | 1052 | 90 | 60 | 720 |  | 60 |  |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NA | NA | 11.40% | NA | 2013 | 150 | 39.4 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 150 |  | 0 | 0
5791030 | HPSS 5791030 | 225 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.36% | NA | 2008 | 102 | 24.86 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 102 |  | 0 | 0
21254 | Inlet 029-R-005 | 250 | 3 |  | 1361 | 108 | 72 | NA |  | 72 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1973 | 140.1 | 48.51 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 140.1 |  | 0 | 0
6769720058 | HPSS 6769720058 | 250 | 3 |  | 1361 | 120 | 80 | UNKV |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | YES | NA | NA | 5.51% | NA | 1979 | 14 | 44.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
38128 | 029-V-017, 018, 019 | 250 | 3 |  | 1106 | 600 | 1 | 720 |  | 1 |  |  | UNVALID | 4.5 | 0.237 | 35000 | 0.6 | NO | NO | YES | 6.78% | 6.78% | 1990 | 0 | 40.28 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 0 |  | 0 | 0
55927 | Inlet 029-R-043 | 250 | 3 |  | 877 | 160 | 106 | 720 |  | 106 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 8.45% | 1999 | 20.5 | 37.55 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 20.5 |  | 0 | 0
12442 | Inlet 029-R-039 | 225 | 3 |  | 2123 | 90 | 64 | UNKV |  | 64 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NO | YES | 3.18% | 3.18% | 1966 | 35.4 | 42.68 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 35.4 | 0 |  | 0 | 0
3400141 | Inlet 029-R-052 | 250 | 3 |  | 1361 | 252 | 168 | 720 |  | 168 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2009 | 39.5 | 29.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 39.5 |  | 0 | 0
1045 | Inlet 029-R-040 | 150 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 14.34% | NA | 1967 | 12 | 87.34 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 12 | 0 |  | 0 | 0
57519-IN | Inlet 029-R-012 | 400 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 12.85% | 12.85% | 1966 | 34.4 | 86.85 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 34.4 | 0 |  | 0 | 0
30C1115 | Inlet 029-R-037 | 225 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 7.23% | NA | 1957 | 40.1 | 83.73 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 40.1 | 0 |  | 0 | 0
PRE-CNG (Inlet 029-R- | Inlet 029-R-053 | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1962 | 94.2 | 79.53 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 94.2 | 0 |  | 0 | 0
PRE-CNG (Inlet 029-R- | Inlet 029-R-054 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 8.03% | 1962 | 215.6 | 80.53 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 215.6 | 0 |  | 0 | 0
UNKV (Inlet 029-R-028 & | Inlet 029-R-028 & 029-R-055 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 1983 | 1571.5 | 83.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 1571.5 |  | 0 | 0
956 | HPSS 956 | 250 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 15.02% | NA | 1981 | 28 | 77.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 28 |  | 0 | 0
5790920 | HPSS 5790920 | 225 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1957 | 27.8 | 65.86 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 27.8 | 0 |  | 0 | 0
5790915 | Service Stub | 225 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.36% | 4.36% | 1965 | 3 | 57.86 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 3 | 0 |  | 0 | 0
PRE-CNG (Outlet 029-R- | Outlet 029-R-054 | 100 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 3.21% | 3.21% | 1962 | 569.2 | 64.71 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 569.2 | 0 |  | 0 | 0
5791380 | HPSS 5791380 | 225 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1967 | 8 | 55.86 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 8 | 0 |  | 0 | 0
3230510426 | HPSS 3230510426 | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1978 | 48 | 48.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 48 |  | 0 | 0
7350020700 | HPSS 7350020700 | 225 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1996 | 15 | 38.86 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 15 |  | 0 | 0
230251 | Inlet 029-R-068 | 250 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2016 | 67.1 | 45.78 | Addressed w/ 116 Segment | 2018 | 1 | 1 | 0 | 67.1 |  | 0 | 0
200195 | Inlet 029-R-064 | 250 | 3 |  | 1361 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2013 | 25.6 | 42.51 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25.6 |  | 0 | 0
233792 | Inlet 029-R-069 | 400 | 3 |  | 1106 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 4.5 | 0.237 | 42000 | 0.6 | NO | NO | YES | 9.04% | 10.85% | 2016 | 42 | 51.35 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 42 |  | 0 | 0
188984 | Inlet 029-R-060 | 400 | 3 |  | 1361 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 2012 | 38 | 46.31 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 38 |  | 0 | 0
2535 | Inlet 029-R-028 | 250 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 1994 | 11 | 58.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 11 |  | 0 | 0
55804 | Inlet 029-R-005 | 250 | 3 |  | 933 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 1998 | 24.8 | 56.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 24.8 |  | 0 | 0
41294 | 029-O-012 | 500 | 3 |  | 794 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NA | NA | 25.17% | NA | 1991 | 54 | 98.17 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 54 |  | 0 | 0
15768 | 4" Wheeler H.P. Loop Line | 250 | 3 |  | 877 | 0 | 0 | 250 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1969 | 2240 | 76.55 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 2240 | 0 |  | 0 | 0
6489893371 | HPSS 6489893371 | 400 | 3 |  | 1820 | 780 | 520 | 720 |  | 520 | X | Service | VALID | 1.315 | 0.133 | 30000 | 0.6 | NO | NA | NA | 6.59% | NA | 2013 | 12 | 23.59 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 12 | 1 | 0 | 12 |  | 1
7103782579 | HPSS 7103782579 | 250 | 3 |  | 3539 | 600 | 400 | 1440 |  | 400 | X | Service | VALID | 1.315 | 0.133 | 35000 | 1 | NO | NA | NA | 3.53% | NA | 2017 | 0 | 11.53 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
57C9412 | 6" South Moses Lake H.P. Line | 250 | 3 |  | 544 | 450 | 300 | NA |  | 300 | X | NA | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 18.35% | 1965 | 15666.8 | 88.35 | Accept Most Stringent Criteria | -- | 1 | 0 | 15666.8 | 0 | 1 | 15666.8 | 0 | 1
54006 | 6" West Wheeler H.P. Line | 250 | 3 |  | 794 | 755 | 503 | 720 |  | 503 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 12.59% | 9.98% | 1997 | 184 | 43.59 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 184 | 1 | 0 | 184 |  | 1
24872 | 6" Quincy H.P. Line | 250 | 3 |  | 544 | 600 | 400 | NA |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 18.35% | 1977 | 370.9 | 63.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 370.9 | 1 | 0 | 370.9 |  | 1
30122 | 6" South Moses Lake H.P. Line | 250 | 3 |  | 544 | 400 | 266 | 250 |  | 250 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 18.35% | 1982 | 5715.6 | 69.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5715.6 | 1 | 0 | 5715.6 |  | 1
48598 | 6" West Wheeler H.P. Line | 250 | 3 |  | 544 | 600 | 400 | 275 |  | 275 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 18.35% | 1995 | 1044.7 | 60.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1044.7 | 1 | 0 | 1044.7 |  | 1
50340 | 6" West Quincy H.P. Line | 250 | 3 |  | 544 | 600 | 400 | 275 |  | 275 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 9.46% | 18.35% | 1996 | 5550 | 62.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 5550 | 1 | 0 | 5550 |  | 1
54843 | 6" North Moses Lake H.P. Line | 250 | 3 |  | 544 | 750 | 500 | 275 |  | 275 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 18.35% | 1998 | 40205.4 | 71.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 40205.4 | 1 | 0 | 40205.4 |  | 1
39111 | 6" Othello H.P. Loop Line | 400 | 3 |  | 933 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.188 | 42000 | 0.8 | NO | YES | YES | 16.78% | 13.52% | 1990 | 13732.3 | 69.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 13732.3 | 1 | 0 | 13732.3 |  | 1
36182 | 6" Othello H.P. Loop Line | 400 | 3 |  | 933 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.188 | 42000 | 0.8 | NO | YES | YES | 16.78% | 13.52% | 1989 | 37806.1 | 74.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 37806.1 | 1 | 0 | 37806.1 |  | 1
20285 | 6" Wenatchee H.P. Line | 225 | 3 |  | 544 | 750 | 500 | NA |  | 500 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 11.33% | 16.52% | 1973 | 637.9 | 67.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 637.9 | 1 | 0 | 637.9 |  | 1
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
33819 | Main to M&R 37072, 029-R-018 | 400 | 3 |  | 758 | 750 | 500 | NA |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 13.68% | 15.82% | 1986 | 569.6 | 60.32 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 569.6 | 1 | 0 | 569.6 |  | 1
161308 | 4" N. Wheeler H.P. Line | 250 | 3 |  | 492 | 678 | 452 | NA |  | 452 | X | X | VALID | 4.5 | 0.154 | 24000 | 0.6 | NO | YES | YES | 15.22% | 15.02% | 2009 | 3969.9 | 50.72 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3969.9 | 1 | 0 | 3969.9 |  | 1
33681 | 4" Othello Transmission Line | 400 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 13.68% | 12.85% | 1986 | 103.8 | 54.18 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 103.8 | 1 | 0 | 103.8 |  | 1
36411 | 4" Othello Transmission Line | 400 | 3 |  | 877 | 750 | 500 | NA |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 13.68% | NA | 1988 | 116.4 | 49.18 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 116.4 | 1 | 0 | 116.4 |  | 1
48599 | 6" West Wheeler H.P. Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1995 | 51 | 34.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 51 | 1 | 0 | 51 |  | 1
58763 | 2" Wheeler H.P. Line | 250 | 3 |  | 877 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 2001 | 672.2 | 36.55 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 672.2 | 1 | 0 | 672.2 |  | 1
48639 | Wheeler H.P. Distribution System | 250 | 3 |  | 933 | 660 | 440 | 1440 |  | 440 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1995 | 1498.4 | 45.53 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1498.4 | 1 | 0 | 1498.4 |  | 1
189195 | 4" South Moses Lake H.P. Line | 250 | 3 |  | 1052 | 750 | 500 | 720 |  | 500 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 7.12% | 6.78% | 2012 | 164 | 29.62 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 164 | 1 | 0 | 164 |  | 1
192292 | 6" West Quincy H.P. Line | 250 | 3 |  | 1052 | 710 | 473 | 720 |  | 473 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 7.12% | 6.78% | 2012 | 1506.6 | 32.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1506.6 | 1 | 0 | 1506.6 |  | 1
25322 | Wheeler H.P. Distribution System | 250 | 3 |  | 1193 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 6.28% | 1977 | 1174.6 | 52.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1174.6 | 1 | 0 | 1174.6 |  | 1
30357 | Inlet 029-R-055 | 250 | 3 |  | NA | NA | NA | 400 |  | 400 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1983 | 0 | 27 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
164908 | Inlet 029-R-057 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X | Service | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2009 | 0 | 14 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
2219720022 | 029-O-010 | 250 | 3 |  | 418 | 750 | 500 | 275 |  | 275 | X | Service | VALID | 6.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 18.35% | 23.89% | 1998 | 31.1 | 62.39 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 31.1 | 1 | 0 | 31.1 |  | 1
234314 | Inlet 029-R-071 | 400 | 3 |  | 1361 | 750 | 500 | 720 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 2016 | 83 | 24.31 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 83 | 1 | 0 | 83 |  | 1
207109 | 029-O-011, 029-R-065 | 150 | 3 |  | 2269 | 225 | 150 | 275 |  | 150 | X | X | VALID | 2.375 | 0.154 | 35000 | 1 | NO | NO | NO | 3.30% | 3.30% | 2013 | 4 | 13.3 | No Action Needed | -- | 1 | 1 | 0 | 4 | 1 | 0 | 4 |  | 1
181660-IN | Inlet 029-R-058 | 500 | 3 |  | 1643 | 1440 | 960 | 1440 |  | 960 | X | X | VALID | 4.5 | 0.237 | 52000 | 0.6 | NO | NO | YES | 9.13% | 11.38% | 2011 | 6 | 34.38 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6 | 1 | 0 | 6 |  | 1
181660-OUT | Outlet 029-R-058 | 400 | 3 |  | 1106 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.25 | 42000 | 0.8 | NO | NO | YES | 12.62% | 13.52% | 2011 | 90.9 | 36.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 90.9 | 1 | 0 | 90.9 |  | 1
54919 | Inlet 029-R-044 | 250 | 3 |  | 1183 | 750 | 500 | 720 |  | 500 | X | X | VALID | NA | NA | NA | NA | NO | NO | YES | NA | 8.45% | 1998 | 8 | 32.95 | No Action Needed | -- | 1 | 1 | 0 | 8 | 1 | 0 | 8 |  | 1
3400700 | Inlet 029-R-044 | 250 | 3 |  | 499 | 750 | 500 | NA |  | 499 | X | Service | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 1998 | 161 | 49.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 161 | 1 | 0 | 161 |  | 1
1395 | Service Stub (029-V-060) | 250 | 3 |  | 499 | 790 | 526 | NA |  | 499 | X | Service | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 2001 | 666.9 | 52.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 666.9 | 1 | 0 | 666.9 |  | 1
3400139 | 029-V-060 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 2001 | 0 | 18 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
7429080852 | Inlet 029-R-059 | 250 | 3 |  | 499 | 850 | 566 | 275 |  | 275 | X | Service | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 15.02% | NA | 2011 | 253 | 43.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 253 | 1 | 0 | 253 |  | 1
28667 | Inlet 029-R-022 | 400 | 3 |  | 1361 | 750 | 500 | 500 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1981 | 382 | 42.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 382 | 1 | 0 | 382 |  | 1
3740200 | 029-R-022 | 400 | 3 |  | 933 | 750 | 500 | NA |  | 500 | X | Service | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 12.85% | NA | 1981 | 1570 | 62.35 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1570 | 1 | 0 | 1570 |  | 1
49145 | Inlet 029-R-033 | 400 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1995 | 80.7 | 34.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 80.7 | 1 | 0 | 80.7 |  | 1
50223 | Inlet 029-R-049 | 400 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 1996 | 81.6 | 34.31 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 81.6 | 1 | 0 | 81.6 |  | 1
37943 | Inlet 029-R-025 | 250 | 3 |  | 877 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1990 | 63.4 | 37.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 63.4 | 1 | 0 | 63.4 |  | 1
40785 | Inlet 029-R-063 | 250 | 3 |  | 933 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 1991 | 116 | 41.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 116 | 1 | 0 | 116 |  | 1
192354 | Inlet 029-R-061 | 225 | 3 |  | 1183 | 600 | 400 | 720 |  | 400 | X | X | VALID | 6.625 | 0.188 | 52000 | 1 | NO | NO | YES | 7.62% | 7.61% | 2013 | 67.6 | 24.62 | No Action Needed | -- | 1 | 1 | 0 | 67.6 | 1 | 0 | 67.6 |  | 1
57519-OUT | Outlet 029-R-012 | 100 | 3 |  | 499 | 150 | 107 | NA |  | 107 | X | NA | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 6.01% | 6.01% | 1966 | 732.1 | 58.51 | Accept Most Stringent Criteria | -- | 1 | 0 | 732.1 | 0 | 1 | 732.1 | 0 | 1
400 | Inlet M&R 31551 | 100 | 3 |  | 499 | 150 | 107 | NA |  | 107 | X | Service | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 6.01% | NA | 1966 | 94 | 53.51 | Accept Most Stringent Criteria | -- | 1 | 0 | 94 | 0 | 1 | 94 | 0 | 1
235111 | 6" Quincy H.P. Line (029-V-098) | 250 | 3 |  | 1758 | 620 | 413 | 720 |  | 413 | X | X | VALID | 6.625 | 0.28 | 52000 | 0.8 | NO | NO | YES | 5.69% | 5.69% | 2016 | 31.3 | 21.19 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 31.3 | 1 | 0 | 31.3 |  | 1
51291 | Inlet 029-R-035 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1993 | 19.4 | 32.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 19.4 | 1 | 0 | 19.4 |  | 1
49695 | 4" N. Wheeler H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1995 | 31.1 | 31.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 31.1 | 1 | 0 | 31.1 |  | 1
53921 | Inlet 029-R-045 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1999 | 79.9 | 29.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 79.9 | 1 | 0 | 79.9 |  | 1
55540 | Inlet 029-R-041 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1998 | 32.9 | 30.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 32.9 | 1 | 0 | 32.9 |  | 1
194667 | Main to HPSS 1571530516 | 250 | 3 |  | 1361 | 690 | 460 | 720 |  | 460 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2012 | 475 | 24.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 475 | 1 | 0 | 475 |  | 1
196743 | Inlet 029-R-064 | 250 | 3 |  | 1361 | 740 | 493 | 720 |  | 493 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2012 | 68 | 23.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 68 | 1 | 0 | 68 |  | 1
200620 | Inlet 029-R-063 | 250 | 3 |  | 1361 | 600 | 400 | 720 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2013 | 24 | 22.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 24 | 1 | 0 | 24 |  | 1
232225 | Inlet 029-R-070 | 250 | 3 |  | 1361 | 600 | 400 | 720 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2016 | 21.9 | 21.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 21.9 | 1 | 0 | 21.9 |  | 1
223306 | Inlet 029-R-066 | 225 | 3 |  | 1193 | 650 | 433 | 720 |  | 433 | X | X | VALID | 1.315 | 0.133 | 35000 | 0.6 | NO | YES | YES | 3.18% | 5.66% | 2015 | 6.3 | 25.66 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6.3 | 1 | 0 | 6.3 |  | 1
3400141 (OUT) | Outlet 029-R-052 | 150 | 3 |  | 945 | 252 | 168 | NA |  | 168 | X | Service | VALID | 2.375 | 0.156 | 24000 | 0.6 | NO | NA | NA | 4.76% | NA | 2009 | 578.5 | 27.76 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 578.5 | 1 | 0 | 578.5 |  | 1
7429080852 (OUT) | Outlet 029-R-059 | 100 | 3 |  | 873 | 250 | 166 | NA |  | 166 | X | Service | VALID | 4.5 | 0.156 | 42000 | 0.6 | NO | NA | NA | 3.43% | NA | 2011 | 46 | 16.43 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 46 | 1 | 0 | 46 |  | 1
4882181722 | HPSS 4882181722 | 250 | 3 |  | 3539 | 755 | 503 | UNKV |  | 503 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 1 | YES | NA | NA | 3.53% | NA | 2017 | 0 | 11.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 0 |  | 0 | 0
5851521 | HPSS 5851521 | 225 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 2009 | 10.8 | 22.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10.8 |  | 0 | 0
3660004 | HPSS 3660004 | 400 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 12.85% | 12.85% | 1984 | 127.4 | 54.35 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 127.4 |  | 0 | 0
3660050 | HPSS 3660050 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1964 | 72 | 57.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 72 | 0 |  | 0 | 0
3660001 | HPSS 3660001 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1989 | 334 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 334 |  | 0 | 0
3660040 | HPSS 3660040 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 161.6 | 40.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 161.6 |  | 0 | 0
3660048 | HPSS 3660048 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 51 | 38.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
3660028 | HPSS 3660028 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 8 | 38.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
3660026 | HPSS 3660026 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1994 | 119 | 39.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 119 |  | 0 | 0
3660060 | HPSS 3660060 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 2005 | 52 | 32.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
3260173 | HPSS 3260173 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2001 | 12.7 | 33.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12.7 |  | 0 | 0
2345129510 | HPSS 2345419510 | 250 | 3 |  | 1193 | 770 | 513 | UNKV |  | 513 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2011 | 10 | 28.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
1571530516 | HPSS 1571530516 | 250 | 3 |  | 1193 | 685 | 456 | UNKV |  | 456 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NO | YES | 6.28% | 5.51% | 2012 | 6 | 27.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
9206776340 | HPSS 9206776340 | 250 | 3 |  | 1193 | 680 | 453 | UNKV |  | 453 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2015 | 26 | 26.28 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 26 |  | 0 | 0
3400118 | HPSS 3400118 | 250 | 3 |  | 1214 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 6.18% | NA | 1996 | 13.5 | 35.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13.5 |  | 0 | 0
3261539 | HPSS 3261539 | 250 | 3 |  | 1214 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 6.18% | NA | 2009 | 8.9 | 29.18 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8.9 |  | 0 | 0
5790185 | HPSS 5790185 | 225 | 3 |  | 1193 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | YES | YES | 5.66% | 5.66% | 1972 | 92 | 47.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 92 |  | 0 | 0
3023854651 | HPSS 3023854651 | 225 | 3 |  | 1193 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 5.66% | NA | 2014 | 18 | 26.16 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
3261560 | HPSS 3261560 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1981 | 6.1 | 36.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6.1 |  | 0 | 0
3261540 | HPSS 3261540 | 250 | 3 |  | 1549 | 680 | 453 | UNKV |  | 453 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 10 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
3370113 | HPSS 3370113 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 16 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
3762740 | HPSS 3762740 | 250 | 3 |  | 1549 | 640 | 426 | UNKV |  | 426 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2006 | 100 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 100 |  | 0 | 0
5881077387 | HPSS 5881077387 | 250 | 3 |  | 1549 | 770 | 513 | UNKV |  | 513 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2011 | 74.5 | 21.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 74.5 |  | 0 | 0
5790940 | HPSS 5790940 | 225 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1957 | 17 | 55.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 17 | 0 |  | 0 | 0
5790200 | HPSS 5790200 | 225 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1960 | 11.9 | 52.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 11.9 | 0 |  | 0 | 0
5790222 | HPSS 5790222 | 225 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1979 | 9 | 37.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
5790898 | HPSS 5790898 | 225 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.36% | 4.36% | 1984 | 90.2 | 34.86 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 90.2 |  | 0 | 0
5790233 | HPSS 5790233 | 225 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1991 | 42.3 | 31.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.3 |  | 0 | 0
5790251 | HPSS 5790251 | 225 | 3 |  | 1549 | 635 | 423 | UNKV |  | 423 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1997 | 133 | 29.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 133 |  | 0 | 0
5790252 | HPSS 5790252 | 225 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.36% | NA | 1997 | 99 | 28.36 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 99 |  | 0 | 0
6727483958 | HPSS 6727483958 | 250 | 3 |  | 2123 | 707 | 471 | UNKV |  | 471 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 3.53% | NA | 2012 | 16.3 | 16.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.3 |  | 0 | 0
3740178 | HPSS 3740178 | 100 | 3 |  | 933 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 3.21% | 3.21% | 1999 | 21 | 26.21 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
33C9263 | 6" Quincy H.P. Line | 250 | 3 |  | 544 | 560 | 373 | UNKV |  | 373 | X | NA | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 18.35% | 18.35% | 1965 | 90004.4 | 98.35 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 90004.4 | 0 |  | 0 | 0
45477 | 6" Quincy H.P. Line | 250 | 3 |  | 499 | 600 | 400 | UNKV |  | 400 | X | NA | UNVALID | 8.625 | 0.28 | 35000 | 0.8 | YES | YES | YES | 18.35% | 18.35% | 1965 | 2389.3 | 80.85 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 2389.3 | 0 |  | 0 | 0
21601 | 6" Quincy H.P. Line | 250 | 3 |  | 544 | 750 | 500 | UNKV |  | 500 | X | X | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | YES | YES | YES | 12.59% | 18.35% | 1973 | 1299.4 | 71.85 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1299.4 |  | 0 | 0
33C9263 | 6" Quincy H.P. Line | 250 | 3 |  | 544 | 560 | 373 | UNKV |  | 373 | X | NA | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 18.35% | 18.35% | 1965 | 90004.4 | 98.35 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 90004.4 | 0 |  | 0 | 0
19482 | 4" Wheeler H.P. Loop Line | 250 | 3 |  | 499 | 750 | 500 | UNKV |  | 499 | X |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 15.02% | 15.02% | 1971 | 1840.9 | 69.52 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1840.9 |  | 0 | 0
O0074586 | 6" Wenatchee H.P. Line | 225 | 3 |  | 953 | 600 | 400 | UNKV |  | 400 | X | X | UNVALID | 6.625 | 0.188 | 42000 | 0.8 | YES | YES | YES | 9.44% | 7.61% | 2005 | 38.4 | 34.44 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38.4 |  | 0 | 0
3400459 | Inlet 029-R-057 | 250 | 3 |  | 499 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | YES | YES | 15.02% | 15.02% | 1996 | 1301 | 57.02 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1301 |  | 0 | 0
3660055 | 029-R-051, M&R O0083324 | 400 | 3 |  | 933 | 780 | 520 | UNKV |  | 520 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 12.85% | NA | 2008 | 37.4 | 41.35 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 37.4 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
O0082714 | 8" REC Silicon Reinforcement | 250 | 3 |  | 418 | 615 | 410 | UNKV |  | 410 | X |  | UNVALID | 8.625 | 0.25 | 52000 | 0.8 | YES | YES | YES | 8.29% | 23.89% | 2007 | 927.8 | 62.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 927.8 |  | 0 | 0
3400130 | 1329 E Wheeler Rd | 250 | 3 |  | 933 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 8.03% | 1960 | 372.8 | 62.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 372.8 | 0 |  | 0 | 0
3400124 | Inlet 029-R-030 | 250 | 3 |  | 933 | 660 | 440 | UNKV |  | 440 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1995 | 12 | 38.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
O0067106 | Inlet 029-R-067 | 250 | 3 |  | 1214 | 750 | 500 | UNKV |  | 500 | X |  | UNVALID | 1.66 | 0.14 | 35000 | 0.6 | YES | YES | YES | 4.23% | 6.18% | 1998 | 95.4 | 34.68 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 95.4 |  | 0 | 0
1145 | Inlet M&R 50342 | 250 | 3 |  | 544 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 18.35% | 18.35% | 1996 | 488.7 | 53.85 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 488.7 |  | 0 | 0
58601 | HPSS 3764572 | 250 | 3 |  | 2260 | 500 | 333 | 1200 |  | 333 | X |  | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | NO | NA | NA | 3.32% | NA | 1999 | 5 | 22.32 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 5 |  | 0 | 0
180809 | 6" North Moses Lake H.P. Line | 250 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 7.12% | 15.02% | 2011 | 4875 | 49.52 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 4875 |  | 0 | 0
44879 | 4" Othello Transmission Line | 400 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 13.68% | 10.05% | 1993 | 60 | 49.68 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 60 |  | 0 | 0
O0083214 | 2" Wheeler H.P. Line | 250 | 3 |  | 1361 | 640 | 426 | 1440 |  | 426 | X |  | UNVALID | 2.375 | 0.154 | 42000 | 0.6 | NO | NO | YES | 4.59% | 5.51% | 2008 | 57.2 | 25.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 57.2 |  | 0 | 0
42827 | 029-V-024 | 250 | 3 |  | NA | NA | NA | 720 |  | 720 | X |  | UNVALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1992 | 0 | 22.5 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 0 |  | 0 | 0
20757 | 4" Wheeler H.P. Loop Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1972 | 99.8 | 46.05 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 99.8 |  | 0 | 0
237006 | 6" Quincy H.P. Line | 250 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 6.625 | 0.28 | 52000 | 0.8 | NO | YES | YES | 5.69% | 15.02% | 2016 | 760 | 44.52 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 760 |  | 0 | 0
50648 | Inlet 029-R-057 | 250 | 3 |  | 794 | 800 | 533 | 720 |  | 533 | X |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 12.59% | 8.45% | 1996 | 263 | 48.09 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 263 |  | 0 | 0
21940 | Inlet 029-R-018 | 400 | 3 |  | 1321 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 9.08% | 8.81% | 1973 | 1347.9 | 57.58 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1347.9 |  | 0 | 0
60612 | Inlet 029-R-008 | 400 | 3 |  | 1361 | 750 | 500 | NA |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 2001 | 13.4 | 31.81 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 13.4 |  | 0 | 0
20799 | Inlet 029-R-014 | 250 | 3 |  | 877 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 8.55% | NA | 1972 | 227.1 | 47.05 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 227.1 |  | 0 | 0
32315 | 4" Wheeler H.P. Loop Line | 250 | 3 |  | 877 | 400 | 266 | 720 |  | 266 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NA | NA | 8.55% | NA | 1985 | 28 | 39.55 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 28 |  | 0 | 0
21209 | Main Stub | 225 | 3 |  | 933 | 720 | 480 | 1440 |  | 480 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 4.96% | 7.23% | 1973 | 1 | 48.23 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1 |  | 0 | 0
O0085074 | Inlet 029-R-056 | 250 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2008 | 41 | 25.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 41 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
40C4357 | 8" Yakima H.P. Line | 200 | 3 |  | 418 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 19.12% | 19.12% | 1997 | 4864.1 | 80.7 | 116 Segment, Most Stringent Criteria | 2016 | 1 | 1 | 0 | 4864.1 |  | 0 | 0
YakimaL5-1 | 6" Toppenish-Zillah Transmission Line | 400 | 3 |  | 499 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | YES | YES | YES | 29.37% | 29.37% | 1956 | 32334.3 | 165.87 | 116 Segment, Pressure Test | 2019 | 1 | 0 | 32334.3 | 0 |  | 0 | 0
YakimaL5-1 | 6” Toppenish-Zillah H.P. Line | 400 | 3 |  | 544 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | NA | NA | 29.37% | NA | 1956 | 10.9 | 145.87 | 116 Segment, Pressure Test | 2019 | 1 | 0 | 10.9 | 0 |  | 0 | 0
Fish_968 | 8" Yakima H.P. Line | 200 | 3 |  | 418 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.188 | 24000 | 0.8 | NO | YES | YES | 19.12% | 19.12% | 1956 | 2399.5 | 110.62 | 116 Segment, Replace | 2019 | 1 | 0 | 2399.5 | 0 |  | 0 | 0
FISH_968_Lat_26 | 8" Yakima H.P. Line | 200 | 3 |  | 1113 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.5 | 24000 | 0.8 | NO | NA | NA | 7.19% | NA | 1956 | 695 | 89.69 | 116 Segment, Replace | 2019 | 1 | 0 | 695 | 0 |  | 0 | 0
20375 | 8" Yakima H.P. Line (Inlet 032-R-003) | 200 | 3 |  | 1045 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 8.625 | 0.25 | 46000 | 0.8 | NO | NO | YES | 7.50% | 7.65% | 1973 | 1578.7 | 72.15 | 116 Segment, Retire | 2019 | 1 | 1 | 0 | 1578.7 |  | 0 | 0
47C8256 | 3" Prosser H.P. Line | 250 | 3 |  | 1169 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.8 | NO | NO | YES | 8.55% | 6.78% | 1964 | 210.7 | 75.05 | 116 Segment, Retire | 2020 | 1 | 0 | 210.7 | 0 |  | 0 | 0
YakimaL4-1 | 3” Prosser H.P. Line | 250 | 3 |  | 641 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 11.69% | 11.69% | 1956 | 5821.1 | 105.69 | 116 Segment, Retire | 2020 | 1 | 0 | 5821.1 | 0 |  | 0 | 0
Fish-L6-1 | 3” Zillah H.P. Line | 175 | 3 |  | 641 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 4.99% | 8.18% | 1956 | 855.7 | 90.68 | 116 Segment, Replace | 2020 | 1 | 0 | 855.7 | 0 |  | 0 | 0
Fish-L7-1 | 4” Wapato H.P. Line | 152 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 9.13% | 9.13% | 1956 | 32876.1 | 106.63 | 116 Segment, Pressure Test | 2020 | 1 | 0 | 32876.1 | 0 |  | 0 | 0
15420 | 3" Sunnyside H.P. Line | 200 | 3 |  | 641 | 150 | 107 | NA |  | 107 |  | NA | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 9.35% | NA | 1969 | 253.3 | 59.85 | 116 Segment, Replace | 2021 | 1 | 0 | 253.3 | 0 |  | 0 | 0
21440 | 3" Sunnyside H.P. Line | 200 | 3 |  | 499 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 6.84% | 12.02% | 1974 | 93.6 | 77.52 | 116 Segment, Replace | 2021 | 1 | 1 | 0 | 93.6 |  | 0 | 0
Fish-L9-1 | 3” Granger H.P. Line | 175 | 3 |  | 641 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 8.18% | 8.18% | 1956 | 31465.3 | 105.68 | 116 Segment, Replace | 2021-2023 | 1 | 0 | 31465.3 | 0 |  | 0 | 0
Fish-L1-1 | 3” Sunnyside H.P. Line | 200 | 3 |  | 641 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 9.35% | 9.35% | 1956 | 4236.4 | 94.42 | 116 Segment, Replace | 2021 | 1 | 0 | 4236.4 | 0 |  | 0 | 0
Fish-L8-1 | 3” South Toppenish H.P. Line | 175 | 3 |  | 641 | 0 | 0 | 400 |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.18% | 8.18% | 1956 | 6141.6 | 95.68 | 116 Segment, Replace | 2022 | 1 | 0 | 6141.6 | 0 |  | 0 | 0
42C2530 | 2" South Sunnyside H.P. Line | 200 | 3 |  | 933 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 6.43% | NA | 1959 | 3995 | 88.45 | 116 Segment, Replace | 2023 | 1 | 0 | 3995 | 0 |  | 0 | 0
6526150 | HPSS 6526150 | 200 | 3 |  | 1193 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 5.03% | NA | 1975 | 10 | 50.03 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 10 |  | 0 | 0
4120815 | HPSS 4120815 | 250 | 3 |  | 1549 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1967 | 185 | 48.34 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 185 | 0 |  | 0 | 0
4381495 | HPSS 4381495 | 152 | 3 |  | 1549 | 118 | 78 | NA |  | 78 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.94% | NA | 1959 | 208 | 54.44 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 208 | 0 |  | 0 | 0
4381615 | HPSS 4381615 | 152 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.94% | NA | 1996 | 50 | 28.44 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 50 |  | 0 | 0
181048 | Inlet 020-R-060 | 400 | 3 |  | 1052 | 500 | 333 | 1440 |  | 333 |  |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 11.40% | 10.85% | 2011 | 40.5 | 39.4 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 40.5 |  | 0 | 0
181050 | Inlet 020-R-060 | 400 | 3 |  | 1052 | 500 | 333 | 720 |  | 333 |  |  | UNVALID | 4.5 | 0.188 | 42000 | 0.6 | NO | NO | YES | 11.40% | 10.85% | 2011 | 0 | 39.4 | Addressed w/ 116 Segment | 2020 | 1 | 1 | 0 | 0 |  | 0 | 0
4050581 | HPSS 4050581 | 200 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 2003 | 78.9 | 25.87 | Addressed w/ 116 Segment | 2021 | 1 | 1 | 0 | 78.9 |  | 0 | 0
22008 | Inlet 020-R-026 | 175 | 3 |  | 933 | 100 | 1 | 720 |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 5.62% | 5.62% | 1959 | 26.9 | 65.12 | Addressed w/ 116 Segment | 2021-2023 | 1 | 0 | 26.9 | 0 |  | 0 | 0
4290401 | HPSS 4290401 | 175 | 3 |  | 1549 | 40 | 26 | NA |  | 26 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.39% | NA | 1971 | 49.6 | 41.39 | Addressed w/ 116 Segment | 2022 | 1 | 1 | 0 | 49.6 |  | 0 | 0
4290403 | HPSS 4290403 | 175 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.39% | NA | 1971 | 20.5 | 41.39 | Addressed w/ 116 Segment | 2022 | 1 | 1 | 0 | 20.5 |  | 0 | 0
4300080 | HPSS 4300080 | 175 | 3 |  | 1193 | 130 | 86 | NA |  | 86 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 4.40% | NA | 1964 | 48.1 | 49.9 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 48.1 | 0 |  | 0 | 0
4300090 | HPSS 4300090 | 175 | 3 |  | 1549 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 3.39% | 3.39% | 1968 | 111.9 | 45.89 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 111.9 | 0 |  | 0 | 0
4300100 | HPSS 4300100 | 175 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.39% | NA | 1958 | 46 | 54.89 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 46 | 0 |  | 0 | 0
4300120 | HPSS 4300120 | 175 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.39% | NA | 1963 | 48 | 49.89 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 48 | 0 |  | 0 | 0
4060666 | HPSS 4060666 | 200 | 3 |  | 1549 | 120 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 2004 | 88.5 | 25.37 | Addressed w/ 116 Segment | 2023 | 1 | 1 | 0 | 88.5 |  | 0 | 0
4060667 | HPSS 4060667 | 200 | 3 |  | 1549 | 120 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 2006 | 6 | 24.37 | Addressed w/ 116 Segment | 2023 | 1 | 1 | 0 | 6 |  | 0 | 0
29894 | Inlet 032-R-012 | 250 | 3 |  | 499 | 1000 | 1 | 400 |  | 1 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1982 | 79.7 | 61.52 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 79.7 |  | 0 | 0
30425 | 020-O-009, R-034 | 300 | 3 |  | 1361 | 450 | 1 | NA |  | 1 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 6.61% | NA | 1984 | 25 | 43.11 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
4051910 | HPSS 4051910 | 200 | 3 |  | 1549 | 110 | 73 | NA |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1991 | 148.1 | 32.87 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 148.1 |  | 0 | 0
4052076 | HPSS 4052076 | 200 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1997 | 17 | 28.87 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
4060107 | HPSS 4060107 | 200 | 3 |  | 1549 | 110 | 73 | NA |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1978 | 37 | 38.37 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 37 |  | 0 | 0
4060625 | HPSS 4060625 | 200 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1984 | 12 | 35.37 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
6490022 | HPSS 6490022 | 250 | 3 |  | 1549 | 110 | 73 | NA |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1991 | 52 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 52 |  | 0 | 0
6490023 | HPSS 6490023 | 250 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1983 | 273.1 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 273.1 |  | 0 | 0
6490130 | HPSS 6490130 | 250 | 3 |  | 933 | 120 | 80 | 275 |  | 80 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1982 | 334.9 | 50.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 334.9 |  | 0 | 0
6490131 | HPSS 6490131 | 250 | 3 |  | 1549 | 650 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2003 | 17 | 26.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
6490163 | HPSS 6490163 | 250 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1994 | 50 | 31.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
6490226 | HPSS 6490226 | 250 | 3 |  | 1549 | 750 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2008 | 29.9 | 24.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 29.9 |  | 0 | 0
6491001 | HPSS 6491001 | 250 | 3 |  | 1549 | 110 | 73 | NA |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1993 | 21 | 31.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
6492008 | HPSS 6492008 | 250 | 3 |  | 1549 | 650 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2003 | 2 | 26.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
6492022 | HPSS 6492022 | 250 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1997 | 49 | 29.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
6493518 | HPSS 6493518 | 250 | 3 |  | 1549 | 625 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2008 | 42 | 24.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
6542580 | HPSS 6542580 | 200 | 3 |  | 1549 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1966 | 33.3 | 47.37 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 33.3 | 0 |  | 0 | 0
6542610 | HPSS 6542610 | 200 | 3 |  | 1549 | 90 | 60 | NA |  | 60 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1966 | 8 | 47.37 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 8 | 0 |  | 0 | 0
6542670 | HPSS 6542670 | 200 | 3 |  | 1549 | 110 | 78 | NA |  | 78 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1968 | 5 | 45.37 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 5 | 0 |  | 0 | 0
6542808 | HPSS 6542808 | 200 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1972 | 16 | 41.37 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
6542823 | HPSS 6542823 | 200 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1967 | 24 | 46.37 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 24 | 0 |  | 0 | 0
6542830 | HPSS 6542830 | 200 | 3 |  | 1549 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1969 | 16 | 44.37 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 16 | 0 |  | 0 | 0
6542840 | HPSS 6542840 | 200 | 3 |  | 1549 | 100 | 71 | NA |  | 71 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1966 | 18 | 47.37 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 18 | 0 |  | 0 | 0
6542866 | HPSS 6542866 | 200 | 3 |  | 1549 | 120 | 80 | NA |  | 80 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1973 | 10 | 40.87 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
6543340 | HPSS 6543340 | 200 | 3 |  | 1549 | 120 | 85 | NA |  | 85 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1968 | 7 | 45.37 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 7 | 0 |  | 0 | 0
6550104 | HPSS 6550104 | 250 | 3 |  | 1549 | 100 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2009 | 14 | 23.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
6550554 | HPSS 6550554 | 250 | 3 |  | 1549 | 110 | 73 | NA |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1993 | 13.1 | 31.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 13.1 |  | 0 | 0
6553925 | HPSS 6553925 | 250 | 3 |  | 1549 | 750 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2008 | 12 | 24.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
6554110 | HPSS 6554110 | 250 | 3 |  | 1549 | 400 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1988 | 14 | 34.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
6554111 | HPSS 6554111 | 250 | 3 |  | 1549 | 605 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1992 | 22 | 32.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
6554114 | HPSS 6554114 | 250 | 3 |  | 1549 | 628 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2005 | 12.8 | 25.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 12.8 |  | 0 | 0
6554537 | HPSS 6554537 | 250 | 3 |  | 1549 | 650 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2008 | 5.1 | 24.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 5.1 |  | 0 | 0
6554706 | HPSS 6554706 | 250 | 3 |  | 1549 | 650 | 1 | NA |  | 1 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2005 | 68 | 25.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 68 |  | 0 | 0
53549 | Inlet 020-R-010 | 160 | 3 |  | 2123 | 150 | 100 | NA |  | 100 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 2.26% | NA | 1964 | 54.8 | 43.76 | Pressure Test/Replace | 2024-2028 | 1 | 0 | 54.8 | 0 |  | 0 | 0
222188 | Inlet 032-R-025 | 250 | 3 |  | 499 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 2012 | 296.1 | 47.52 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 296.1 |  | 0 | 0
6490142 | Inlet 032-R-046 | 250 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 1994 | 15 | 31.34 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
4240140 | 020-R-021 | 400 | 3 |  | 499 | 90 | 64 | NA |  | 64 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 24.04% | NA | 1969 | 16.2 | 87.54 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 16.2 | 0 |  | 0 | 0
4230124 | HPSS 4230124 | 400 | 3 |  | 1549 | 60 | 42 | UNKV |  | 42 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1968 | 14 | 58.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 14 | 0 |  | 0 | 0
4230125 | HPSS 4230125 | 400 | 3 |  | 1549 | 100 | 66 | UNKV |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1984 | 42 | 48.24 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 42 |  | 0 | 0
4230128 | HPSS 4230128 | 400 | 3 |  | 1549 | 118 | 78 | 1440 |  | 78 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1980 | 42 | 50.24 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 42 |  | 0 | 0
4232100 | HPSS 4232100 | 400 | 3 |  | 1549 | 110 | 73 | 1440 |  | 73 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 2002 | 59 | 39.24 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 59 |  | 0 | 0
6543510 | HPSS 6543510 | 200 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1967 | 55 | 46.37 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 55 | 0 |  | 0 | 0
6543530 | HPSS 6543530 | 200 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1968 | 95 | 45.37 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 95 | 0 |  | 0 | 0
4240130 | Inlet 020-R-019 | 400 | 3 |  | 1193 | 50 | 35 | NA |  | 35 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | NO | NA | NA | 10.05% | NA | 1967 | 7 | 68.05 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 7 | 0 |  | 0 | 0
6543562 | Service Stub | 200 | 3 |  | 1549 | 100 | 66 | NA |  | 66 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 1970 | 95 | 43.37 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 95 | 0 |  | 0 | 0
37344 | Inlet 020-R-039 | 400 | 3 |  | 1193 | 900 | 600 | 250 |  | 250 |  |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 8.81% | 10.05% | 1989 | 20 | 48.05 | Addressed w/ 116 Segment | 2019 | 1 | 1 | 0 | 20 |  | 0 | 0
18687 | 020-O-001 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 11.69% | 15.02% | 1956 | 113.7 | 100.02 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 113.7 | 0 |  | 0 | 0
11180 | Inlet 020-R-028 | 152 | 3 |  | 499 | 0 | 0 | 250 |  | 0 |  |  | UNVALID | 4.5 | NA | NA | NA | NO | YES | YES | NA | 9.13% | 1967 | 17 | 75.63 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 17 | 0 |  | 0 | 0
4381500 | HPSS 4381500 | 152 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.94% | NA | 1966 | 104.5 | 56.44 | Addressed w/ 116 Segment | 2020 | 1 | 0 | 104.5 | 0 |  | 0 | 0
4201510 | HPSS 4201510 | 175 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.39% | NA | 1970 | 105.5 | 52.89 | Addressed w/ 116 Segment | 2021-2023 | 1 | 0 | 105.5 | 0 |  | 0 | 0
42C7053 | Inlet 020-R-009 | 200 | 3 |  | 2123 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | NO | NA | NA | 2.82% | NA | 1964 | 5 | 53.32 | Addressed w/ 116 Segment | 2021 | 1 | 0 | 5 | 0 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
4340165 | Inlet M&R 25803 | 175 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 10.52% | 8.73% | 1957 | 12 | 93.52 | Addressed w/ 116 Segment | 2022 | 1 | 0 | 12 | 0 |  | 0 | 0
5869914040 | HPSS 5869914040 | 200 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 3.87% | NA | 2013 | 2.2 | 29.87 | Addressed w/ 116 Segment | 2023 | 1 | 1 | 0 | 2.2 |  | 0 | 0
46C6883 | 020-O-002, Inlet 020-R-006 | 130 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 4.18% | NA | 1964 | 10.6 | 58.68 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 10.6 | 0 |  | 0 | 0
55590 | 020-O-003 | 250 | 3 |  | 499 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 1956 | 14.5 | 99.02 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 14.5 | 0 |  | 0 | 0
135 | Inlet 032-R-021 | 250 | 3 |  | 933 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1982 | 0 | 64.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 0 |  | 0 | 0
4231500 | HPSS 4231504 | 400 | 3 |  | 1549 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1967 | 19 | 74.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 19 | 0 |  | 0 | 0
42C6202 | Inlet 020-R-014 | 150 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 2.90% | NA | 1962 | 64.7 | 59.4 | Pressure Test/Replace | 2018-2023 | 1 | 0 | 64.7 | 0 |  | 0 | 0
6490010 | Service Stub | 250 | 3 |  | 933 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | YES | YES | 8.03% | 8.03% | 1981 | 55 | 65.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 55 |  | 0 | 0
6490160 | Service Stub | 250 | 3 |  | 933 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 1982 | 17 | 64.53 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 17 |  | 0 | 0
UNKV (Stub Selah) | Stub off 4” Selah H.P. Line | 250 | 3 |  | 499 | 0 | 0 | 275 |  | 0 |  |  | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 1985 | 27.8 | 75.02 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 27.8 |  | 0 | 0
165211 | Inlet 020-R-057 | 250 | 3 |  | 933 | 0 | 0 | 720 |  | 0 |  |  | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 8.03% | NA | 2009 | 9 | 51.03 | Pressure Test/Replace | 2018-2023 | 1 | 1 | 0 | 9 |  | 0 | 0
6490224 | HPSS 6490224 | 250 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 4.84% | 4.84% | 1999 | 81.8 | 37.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 81.8 |  | 0 | 0
6554264 | HPSS 6554264 | 250 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2009 | 5 | 32.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
6554638 | HPSS 6554638 | 250 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 4.84% | NA | 2001 | 65 | 36.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 65 |  | 0 | 0
6554125 | Service Stub | 250 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1995 | 7 | 39.84 | Pressure Test/Replace | 2024-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
25856 | 6" Toppenish-Zillah Transmission Line (020-O-008) | 400 | 3 |  | 794 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NA | NA | 20.14% | NA | 1956 | 31.3 | 112.64 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 31.3 | 0 |  | 0 | 0
4391095 | 6” Toppenish-Zillah H.P. Line (Main Stub) | 400 | 3 |  | 544 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 6.625 | 0.188 | 24000 | 0.8 | NO | NO | YES | 29.37% | 15.97% | 1957 | 12.3 | 134.87 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 12.3 | 0 |  | 0 | 0
4230080 | HPSS 4230080 | 400 | 3 |  | 1549 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | YES | YES | 7.74% | 7.74% | 1969 | 228.1 | 73.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 228.1 | 0 |  | 0 | 0
4230100 | HPSS 4230100 | 400 | 3 |  | 1549 | 0 | 0 | 1440 |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | NO | NA | NA | 7.74% | NA | 1957 | 63 | 84.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 63 | 0 |  | 0 | 0
4230105 | HPSS 4230105 | 400 | 3 |  | 1193 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 10.05% | NA | 1964 | 16 | 86.05 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 16 | 0 |  | 0 | 0
4230112 | HPSS 4230112 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1964 | 45 | 77.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 45 | 0 |  | 0 | 0
4230120 | HPSS 4230120 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1959 | 7 | 82.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 7 | 0 |  | 0 | 0
4230122 | HPSS 4230122 | 400 | 3 |  | 1549 | 0 | 0 | UNKV |  | 0 |  |  | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1965 | 7 | 76.24 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 7 | 0 |  | 0 | 0
160 | Inlet 032-R-007 | 200 | 3 |  | 641 | 0 | 0 | NA |  | 0 |  |  | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | NO | NA | NA | 9.35% | NA | 1957 | 70 | 85.85 | Addressed w/ 116 Segment | 2019 | 1 | 0 | 70 | 0 |  | 0 | 0
37647 | 4" Grandview H.P. Line | 250 | 3 |  | 933 | 600 | 400 | 720 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 8.03% | 1989 | 109.9 | 42.03 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 109.9 | 1 | 0 | 109.9 |  | 1
45400 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1994 | 42 | 32.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 42 | 1 | 0 | 42 |  | 1
52929 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 604 | 402 | 1440 |  | 402 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1997 | 324.4 | 31.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 324.4 | 1 | 0 | 324.4 |  | 1
28013 | 020-V-038 | 200 | 3 |  | NA | NA | NA | 400 |  | 400 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1980 | 0 | 28.5 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
40427 | 020-V-046 | 200 | 3 |  | NA | NA | NA | 720 |  | 720 | X | Service | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1991 | 0 | 23 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
54062 | 020-V-064 | 200 | 3 |  | 1500 | 600 | 400 | 720 |  | 400 | X | X | VALID | 3.5 | 0.25 | 35000 | 0.6 | NO | NA | NA | 4.00% | NA | 1999 | 8 | 23 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 8 | 1 | 0 | 8 |  | 1
213913 | 020-V-094, 095 | 400 | 3 |  | 1052 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 42000 | 0.6 | NO | YES | YES | 11.40% | 10.85% | 2016 | 9473.2 | 45.9 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 9473.2 | 1 | 0 | 9473.2 |  | 1
29252 | 032-O-001 | 250 | 3 |  | 499 | 450 | 300 | NA |  | 300 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1981 | 40.7 | 57.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 40.7 | 1 | 0 | 40.7 |  | 1
32811 | 032-O-002 | 200 | 3 |  | 1045 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.322 | 35000 | 0.8 | NO | NO | YES | 7.65% | 7.65% | 1985 | 42.6 | 38.65 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 42.6 | 1 | 0 | 42.6 |  | 1
30269 | 032-O-003, R-002 | 275 | 3 |  | 877 | 580 | 386 | 720 |  | 386 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 9.40% | 7.46% | 1984 | 57.3 | 40.9 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 57.3 | 1 | 0 | 57.3 |  | 1
44924 | 032-V-060 | 250 | 3 |  | NA | NA | NA | 1440 |  | 1440 | X | X | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1993 | 0 | 22 | No Action Needed | -- | 1 | 1 | 0 | 0 | 1 | 0 | 0 |  | 1
163157 | 3" Granger H.P. Line | 175 | 3 |  | 1643 | 710 | 473 | 720 |  | 473 | X | X | VALID | 4.5 | 0.237 | 52000 | 0.6 | NO | NA | NA | 3.19% | NA | 2010 | 1025.2 | 24.19 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1025.2 | 1 | 0 | 1025.2 |  | 1
51763 | 3" Sunnyside H.P. Line (Inlet 020-R-048) | 200 | 3 |  | 1106 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 4.41% | 5.42% | 1996 | 102.1 | 31.92 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 102.1 | 1 | 0 | 102.1 |  | 1
32472 | 4" East Toppenish H.P. Line | 400 | 3 |  | 1106 | 720 | 480 | 720 |  | 480 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.8 | NO | YES | YES | 13.68% | 13.52% | 1986 | 9486.5 | 63.18 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 9486.5 | 1 | 0 | 9486.5 |  | 1
225882 | 4" Grandview H.P. Line | 250 | 3 |  | 1106 | 791 | 527 | 720 |  | 527 | X | X | VALID | 4.5 | 0.188 | 52000 | 0.6 | NO | NO | YES | 5.75% | 6.78% | 2015 | 4967.8 | 30.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4967.8 | 1 | 0 | 4967.8 |  | 1
29290 | 4" Moxee H.P. Line | 250 | 3 |  | 499 | 450 | 300 | NA |  | 300 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1981 | 6867.5 | 67.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 6867.5 | 1 | 0 | 6867.5 |  | 1
29775 | 4" Moxee H.P. Line | 250 | 3 |  | 499 | 460 | 306 | 400 |  | 306 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1982 | 32140.2 | 76.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 32140.2 | 1 | 0 | 32140.2 |  | 1
29836 | 4" Moxee H.P. Line | 250 | 3 |  | 1193 | 450 | 300 | 1440 |  | 300 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 6.28% | 1982 | 546.3 | 47.78 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 546.3 | 1 | 0 | 546.3 |  | 1
173437 | 4" Moxee H.P. Line | 250 | 3 |  | 1106 | 820 | 546 | 720 |  | 546 | X | X | VALID | 4.5 | 0.188 | 52000 | 0.6 | NO | YES | YES | 5.75% | 6.78% | 2010 | 292.5 | 30.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 292.5 | 1 | 0 | 292.5 |  | 1
32470 | 4" Prosser H.P. Loop Line | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 6.78% | 1991 | 3401.1 | 48.05 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 3401.1 | 1 | 0 | 3401.1 |  | 1
31948 | 4" Selah H.P. Line | 250 | 3 |  | 499 | 450 | 300 | 275 |  | 275 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 8.55% | 15.02% | 1985 | 20642.9 | 70.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 20642.9 | 1 | 0 | 20642.9 |  | 1
32976 | 4" Selah H.P. Line | 250 | 3 |  | 1106 | 500 | 333 | 1440 |  | 333 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 6.78% | 1992 | 261.8 | 35.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 261.8 | 1 | 0 | 261.8 |  | 1
41175 | 4" Sunnyside H.P. Line | 200 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 6.84% | 5.42% | 1991 | 879.1 | 43.84 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 879.1 | 1 | 0 | 879.1 |  | 1
47208 | 4" Sunnyside H.P. Line | 200 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 9.86% | 12.02% | 1995 | 4612.1 | 54.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 4612.1 | 1 | 0 | 4612.1 |  | 1
179713 | 4" Wapato H.P. Line | 152 | 3 |  | 1106 | 820 | 546 | 720 |  | 546 | X | X | VALID | 4.5 | 0.237 | 52000 | 0.6 | NO | YES | YES | 2.78% | 4.12% | 2012 | 78.1 | 20.62 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 78.1 | 1 | 0 | 78.1 |  | 1
181100 | 4" Wapato H.P. Line | 152 | 3 |  | 1106 | 850 | 566 | 275 |  | 275 | X | X | VALID | 4.5 | 0.237 | 52000 | 0.6 | NO | YES | YES | 2.78% | 4.12% | 2011 | 486.3 | 22.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 486.3 | 1 | 0 | 486.3 |  | 1
28012 | 4" West Sunnyside H.P. Line | 200 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 9.86% | 12.02% | 1980 | 28479.3 | 69.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 28479.3 | 1 | 0 | 28479.3 |  | 1
25237 | 6" Toppenish-Zillah Transmission Line | 400 | 3 |  | 1056 | 600 | 400 | 720 |  | 400 | X | X | VALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 15.14% | 13.52% | 1979 | 1192.8 | 61.64 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1192.8 | 1 | 0 | 1192.8 |  | 1
43436 | 6" Toppenish-Zillah Transmission Line | 400 | 3 |  | 794 | 900 | 600 | 720 |  | 600 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | NO | YES | 20.14% | 13.52% | 1993 | 482.2 | 58.14 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 482.2 | 1 | 0 | 482.2 |  | 1
59553 | 6" Toppenish-Zillah Transmission Line | 400 | 3 |  | 1045 | 750 | 500 | 720 |  | 500 | X | X | VALID | 8.625 | 0.322 | 42000 | 0.8 | NO | NO | YES | 12.76% | 15.31% | 2000 | 124.4 | 44.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 124.4 | 1 | 0 | 124.4 |  | 1
161307 | 6" Toppenish-Zillah Transmission Line | 400 | 3 |  | 1183 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.25 | 52000 | 0.8 | NO | NO | YES | 10.19% | 13.52% | 2010 | 929.8 | 42.02 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 929.8 | 1 | 0 | 929.8 |  | 1
193985 | 6" Toppenish-Zillah Transmission Line | 400 | 3 |  | 1106 | 750 | 500 | 720 |  | 500 | X | X | VALID | 6.625 | 0.28 | 52000 | 0.8 | NO | NO | YES | 9.10% | 10.85% | 2016 | 1839.2 | 38.85 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 1839.2 | 1 | 0 | 1839.2 |  | 1
42417 | 6" Toppenish-Zillah Transmission Line (R-029, R-022) | 400 | 3 |  | 877 | 900 | 600 | 720 |  | 600 | X | X | VALID | 6.625 | 0.188 | 42000 | 0.8 | NO | NO | YES | 16.78% | 13.52% | 1992 | 35 | 49.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35 | 1 | 0 | 35 |  | 1
42417 | 6" Toppenish-Zillah Transmission Line (R-029, R-022) | 400 | 3 |  | 877 | 900 | 600 | 720 |  | 600 | X | X | VALID | 6.625 | 0.188 | 42000 | 0.8 | NO | NO | YES | 16.78% | 13.52% | 1992 | 72 | 49.28 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 72 | 1 | 0 | 72 |  | 1
24187 | 8" Yakima H.P. Line | 200 | 3 |  | 716 | 750 | 500 | 275 |  | 275 | X | X | VALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 9.86% | 11.16% | 1979 | 12.2 | 54.16 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 12.2 | 1 | 0 | 12.2 |  | 1
25569 | 8" Yakima H.P. Line | 200 | 3 |  | 418 | 750 | 500 | NA |  | 418 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 13.11% | 19.12% | 1979 | 292 | 63.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 292 | 1 | 0 | 292 |  | 1
51197 | 8" Yakima H.P. Line | 200 | 3 |  | 418 | 750 | 500 | 720 |  | 418 | X | X | VALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 13.11% | 19.12% | 1981 | 7092.4 | 71.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 7092.4 | 1 | 0 | 7092.4 |  | 1
227290 | 020-V-108 | 152 | 3 |  | 1843 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.237 | 52000 | 1 | NO | NO | NO | 2.78% | 4.12% | 2015 | 25 | 13.12 | No Action Needed | -- | 1 | 1 | 0 | 25 | 1 | 0 | 25 |  | 1
34666 | Inlet 020-R-037 | 200 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 4.41% | NA | 1987 | 19 | 29.41 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 19 | 1 | 0 | 19 |  | 1
170048 | Inlet 020-R-037 | 200 | 3 |  | 933 | 750 | 500 | NA |  | 500 | X | X | VALID | 1.05 | 0.113 | 35000 | 1 | NO | YES | YES | 2.65% | 6.43% | 2009 | 11 | 29.43 | No Action Needed | -- | 1 | 1 | 0 | 11 | 1 | 0 | 11 |  | 1
4201513 | Inlet 020-R-040 | 175 | 3 |  | 933 | 600 | 400 | 720 |  | 400 | X | Service | VALID | 2.375 | 0.154 | 24000 | 0.6 | NO | NA | NA | 5.62% | NA | 1990 | 153.6 | 39.12 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 153.6 | 1 | 0 | 153.6 |  | 1
40274 | Inlet 020-R-041 | 400 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 8.81% | NA | 1991 | 18 | 36.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 18 | 1 | 0 | 18 |  | 1
47971 | Inlet 020-R-046 | 400 | 3 |  | 1361 | 900 | 600 | 1440 |  | 600 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1995 | 76 | 34.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 76 | 1 | 0 | 76 |  | 1
50749 | Inlet 020-R-047 | 175 | 3 |  | 1361 | 600 | 400 | 720 |  | 400 | X | NA | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 3.86% | 3.86% | 1956 | 20.2 | 52.36 | Accept Most Stringent Criteria | -- | 1 | 0 | 20.2 | 0 | 1 | 20.2 | 0 | 1
52716 | Inlet 020-R-049 | 400 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 8.81% | 8.81% | 1997 | 19 | 33.81 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 19 | 1 | 0 | 19 |  | 1
K0069449 | Inlet 020-R-055 | 250 | 3 |  | 728 | 600 | 400 | 720 |  | 400 | X | X | VALID | 4.5 | 0.156 | 35000 | 0.6 | NO | NO | YES | 10.30% | 5.51% | 2003 | 35.1 | 37.3 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 35.1 | 1 | 0 | 35.1 |  | 1
177231 | Inlet 020-R-062 | 250 | 3 |  | 499 | 750 | 500 | 720 |  | 499 | X | X | VALID | 4.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 15.02% | 15.02% | 2012 | 124.1 | 42.52 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 124.1 | 1 | 0 | 124.1 |  | 1
44923 | Inlet 032-R-035 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1993 | 24.1 | 32.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 24.1 | 1 | 0 | 24.1 |  | 1
49570 | Inlet 032-R-039 | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1996 | 36.8 | 31.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 36.8 | 1 | 0 | 36.8 |  | 1
49732 | Inlet 032-R-040 | 250 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1995 | 2914.6 | 39.01 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2914.6 | 1 | 0 | 2914.6 |  | 1
185114 | Inlet 032-R-048 | 250 | 3 |  | 1361 | 780 | 520 | 720 |  | 520 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2011 | 17.3 | 23.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 17.3 | 1 | 0 | 17.3 |  | 1
280 | Inlet M&R 25803 | 175 | 3 |  | NA | NA | NA | 275 |  | 275 | X | Service | VALID | NA | NA | NA | NA | NO | NA | NA | NA | NA | 1957 | 0 | 47.5 | No Action Needed | -- | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1
37016 | Main to HPSS 6490032 | 250 | 3 |  | 1361 | 450 | 300 | 1440 |  | 300 | X | X | VALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1989 | 486.3 | 35.51 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 486.3 | 1 | 0 | 486.3 |  | 1
40426 | Sunnyside H.P. Distribution System | 200 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X | X | VALID | 6.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 10.07% | 14.68% | 1991 | 2062.3 | 59.18 | Accept Most Stringent Criteria | -- | 1 | 1 | 0 | 2062.3 | 1 | 0 | 2062.3 |  | 1
2522737186 | HPSS 2522737186 | 250 | 3 |  | 2123 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 3.53% | NA | 2013 | 23 | 15.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23 |  | 0 | 0
2970502135 | HPSS 2970502135 | 250 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 2012 | 63 | 27.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 63 |  | 0 | 0
4051918 | HPSS 4051918 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1988 | 77.6 | 32.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 77.6 |  | 0 | 0
4230132 | HPSS 4230132 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1988 | 3 | 41.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 3 |  | 0 | 0
4230133 | HPSS 4230133 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1990 | 40 | 40.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
4231541 | HPSS 4231541 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 7 | 38.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
4231941 | HPSS 4231941 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 17 | 37.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
4231949 | HPSS 4231949 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 42 | 37.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
4261096 | HPSS 4261096 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1983 | 65 | 43.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 65 |  | 0 | 0
4261200 | HPSS 4261200 | 400 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1982 | 7 | 44.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
4272263813 | HPSS 4272263813 | 250 | 3 |  | 1456 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.315 | 0.133 | 24000 | 0.6 | YES | NA | NA | 5.15% | NA | 2016 | 2 | 24.65 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
4303041108 | HPSS 4303041108 | 250 | 3 |  | 2123 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 3.53% | NA | 2013 | 18 | 15.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
4669509776 | HPSS 4669509776 | 200 | 3 |  | 2123 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 2.82% | NA | 2015 | 42 | 13.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
5625261802 | HPSS 5625261802 | 200 | 3 |  | 2901 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.315 | 0.109 | 35000 | 1 | YES | NA | NA | 3.45% | NA | 2017 | 15 | 11.45 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
6490150 | HPSS 6490150 | 250 | 3 |  | 933 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1982 | 46 | 44.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
8106982971 | HPSS 8106982971 | 250 | 3 |  | 2123 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.315 | 0.133 | 35000 | 0.6 | YES | NA | NA | 3.53% | NA | 2016 | 11 | 14.03 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
954527945 | HPSS 954527945 | 250 | 3 |  | 2901 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 35000 | 1 | YES | NA | NA | 4.31% | NA | 2017 | 21 | 12.31 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
1860076 | 6" Toppenish-Zillah Transmission Line | 400 | 3 |  | 1056 | 762 | 508 | UNKV |  | 508 | X | X | UNVALID | 6.625 | 0.25 | 35000 | 0.8 | YES | NO | YES | 15.14% | 13.52% | 1972 | 1119.1 | 65.14 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 1119.1 |  | 0 | 0
4230103 | HPSS 4230103 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1976 | 48 | 47.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 48 |  | 0 | 0
4230110 | HPSS 4230110 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 8 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
4230117 | HPSS 4230117 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1987 | 41 | 41.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41 |  | 0 | 0
4230118 | HPSS 4230118 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1973 | 5 | 48.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
4230119 | HPSS 4230119 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1983 | 46 | 43.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
4230123 | HPSS 4230123 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1973 | 46 | 48.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
4231528 | HPSS 4231528 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1992 | 19 | 39.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
4231532 | HPSS 4231532 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1993 | 15 | 38.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
4231914 | HPSS 4231914 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1994 | 42.9 | 38.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.9 |  | 0 | 0
4231945 | HPSS 4231945 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 17 | 37.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
4232010 | HPSS 4232010 | 400 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1997 | 98.1 | 36.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 98.1 |  | 0 | 0
4232053 | HPSS 4232053 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1999 | 17 | 35.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
9450962221 | HPSS 9450962221 | 400 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 10.05% | NA | 2012 | 14.7 | 36.55 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14.7 |  | 0 | 0
890 | Inlet 020-R-012 | 200 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 6.43% | NA | 1990 | 578.1 | 43.93 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 578.1 |  | 0 | 0
1790 | Inlet 020-R-027 | 152 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 4.88% | 4.88% | 1976 | 289.7 | 40.38 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 289.7 |  | 0 | 0
4060600 | Inlet 020-R-031 | 200 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 6.43% | NA | 1981 | 104.7 | 44.43 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 104.7 |  | 0 | 0
4060620 | Inlet 020-R-032 | 200 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 6.43% | 6.43% | 1988 | 561.3 | 44.93 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 561.3 |  | 0 | 0
4060640 | Inlet 020-R-033 | 200 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 6.43% | 6.43% | 1994 | 216 | 37.93 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 216 |  | 0 | 0
2025 | Inlet 020-R-044 | 200 | 3 |  | 1214 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | YES | YES | 4.94% | 4.94% | 1987 | 458 | 34.94 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 458 |  | 0 | 0
6490020 | Inlet 032-R-013 | 250 | 3 |  | 933 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 8.03% | 1982 | 967.5 | 49.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 967.5 |  | 0 | 0
6490140 | Inlet 032-R-019 | 250 | 3 |  | 933 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | YES | YES | 8.03% | 8.03% | 1982 | 41 | 44.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41 |  | 0 | 0
6490025 | Inlet 032-R-041 | 250 | 3 |  | 1193 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1982 | 133.1 | 43.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 133.1 |  | 0 | 0
4340198 | Inlet M&R 46844 | 175 | 3 |  | 933 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 5.62% | NA | 1994 | 5 | 36.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
4230116 | Service Stub | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 7.74% | 7.74% | 1972 | 13 | 49.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
6490157 | Service Stub | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1987 | 45 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
133510822 | HPSS 133510822 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1987 | 39 | 32.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39 |  | 0 | 0
1619727267 | HPSS 1619727267 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2012 | 192 | 22.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 192 |  | 0 | 0
2502 | HPSS 2502 | 200 | 3 |  | 499 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 4.5 | 0.156 | 24000 | 0.6 | YES | NA | NA | 12.02% | NA | 1991 | 112.1 | 50.02 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 112.1 |  | 0 | 0
3777583108 | HPSS 3777583108 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2012 | 12 | 21.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
4050580 | HPSS 4050580 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1982 | 5 | 35.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
4050635 | HPSS 4050635 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1973 | 90 | 39.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 90 |  | 0 | 0
4050640 | HPSS 4050640 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1975 | 46 | 38.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
4050650 | HPSS 4050650 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1956 | 40 | 56.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 40 | 0 |  | 0 | 0
4051900 | HPSS 4051900 | 200 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1980 | 190.1 | 37.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 190.1 |  | 0 | 0
4051921 | HPSS 4051921 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1981 | 21 | 35.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
4051925 | HPSS 4051925 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1988 | 30 | 32.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
4051927 | HPSS 4051927 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1988 | 55 | 32.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
4051930 | HPSS 4051930 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1991 | 49 | 30.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
4051949 | HPSS 4051949 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1992 | 10 | 30.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
4051964 | HPSS 4051964 | 200 | 3 |  | 2260 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 2.65% | NA | 1994 | 10 | 24.15 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
4051988 | HPSS 4051988 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1989 | 15 | 31.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
4052003 | HPSS 4052003 | 200 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1995 | 66 | 28.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 66 |  | 0 | 0
4052039 | HPSS 4052039 | 200 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1996 | 6 | 28.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
4052052 | HPSS 4052052 | 200 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1997 | 46 | 27.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 46 |  | 0 | 0
4052063 | HPSS 4052063 | 200 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1997 | 37 | 27.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 37 |  | 0 | 0
4052114 | HPSS 4052114 | 200 | 3 |  | 499 | 750 | 500 | UNKV |  | 499 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.87% | 12.02% | 1999 | 20.5 | 45.02 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.5 |  | 0 | 0
4052140 | HPSS 4052140 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 2000 | 10 | 26.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
4060106 | HPSS 4060106 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1990 | 30 | 31.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
4060109 | HPSS 4060109 | 200 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 5.03% | NA | 1976 | 399.2 | 45.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 399.2 |  | 0 | 0
4060116 | HPSS 4060116 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1986 | 18 | 33.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
4060119 | HPSS 4060119 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1973 | 16 | 39.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
4060123 | HPSS 4060123 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1975 | 193.1 | 39.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 193.1 |  | 0 | 0
4060124 | HPSS 4060124 | 200 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 6.43% | NA | 1975 | 37 | 46.43 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 37 |  | 0 | 0
4060627 | HPSS 4060627 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1984 | 9 | 34.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
4060641 | HPSS 4060641 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1992 | 21 | 30.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
4060645 | HPSS 4060645 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1981 | 160.9 | 36.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 160.9 |  | 0 | 0
4060655 | HPSS 4060655 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1980 | 18 | 36.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
4060660 | HPSS 4060660 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1981 | 13.5 | 35.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13.5 |  | 0 | 0
4060670 | HPSS 4060670 | 200 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1985 | 110.1 | 34.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 110.1 |  | 0 | 0
4060671 | HPSS 4060671 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1985 | 7 | 33.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
4060672 | HPSS 4060672 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1986 | 9 | 33.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
4060675 | HPSS 4060675 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1990 | 20 | 31.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
4060700 | HPSS 4060700 | 200 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1992 | 29 | 30.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 29 |  | 0 | 0
4121463 | HPSS 4121463 | 250 | 3 |  | 1549 | 900 | 600 | UNKV |  | 600 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 3.8 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 3.8 |  | 0 | 0
4121468 | HPSS 4121468 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1996 | 42.2 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42.2 |  | 0 | 0
4121498 | HPSS 4121498 | 250 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 12 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
4201515 | HPSS 4201515 | 175 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1978 | 178.1 | 37.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 178.1 |  | 0 | 0
4201561 | HPSS 4201561 | 175 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1997 | 298.2 | 28.39 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 298.2 |  | 0 | 0
4230136 | HPSS 4230136 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1991 | 57.1 | 39.74 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.1 |  | 0 | 0
4231965 | HPSS 4231965 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1996 | 23.7 | 37.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23.7 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
4290402 | HPSS 4290402 | 175 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1986 | 2 | 32.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
4291005 | HPSS 4291005 | 400 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1990 | 23 | 40.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 23 |  | 0 | 0
4291020 | HPSS 4291020 | 175 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.39% | 3.39% | 1994 | 38 | 28.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
4291301 | HPSS 4291301 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1992 | 61 | 39.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 61 |  | 0 | 0
4291326 | HPSS 4291326 | 400 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 7.74% | NA | 1998 | 68 | 36.24 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 68 |  | 0 | 0
4300060 | HPSS 4300060 | 175 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1988 | 54 | 31.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
4300070 | HPSS 4300070 | 175 | 3 |  | 1193 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 4.40% | NA | 1964 | 51 | 48.9 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 51 | 0 |  | 0 | 0
4301370 | HPSS 4301370 | 175 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1992 | 55 | 29.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
4301661 | HPSS 4301661 | 175 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1996 | 28 | 27.89 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 28 |  | 0 | 0
4301665 | HPSS 4301665 | 175 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.39% | NA | 1999 | 51 | 26.39 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
4340170 | HPSS 4340170 | 175 | 3 |  | 933 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 5.62% | NA | 1959 | 100 | 60.12 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 100 | 0 |  | 0 | 0
4340195 | HPSS 4340195 | 175 | 3 |  | 1214 | 750 | 535 | UNKV |  | 535 | X | Service | UNVALID | 1.66 | 0.14 | 24000 | 0.6 | YES | NA | NA | 4.32% | NA | 1964 | 53 | 48.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 0 | 53 | 0 |  | 0 | 0
4381498 | HPSS 4381498 | 152 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.94% | NA | 1989 | 16.5 | 30.94 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.5 |  | 0 | 0
4381600 | HPSS 4381600 | 152 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.94% | NA | 1981 | 16.1 | 34.94 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.1 |  | 0 | 0
4381613 | HPSS 4381613 | 152 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 2.94% | NA | 1995 | 49 | 27.94 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
6350403 | HPSS 6350403 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1978 | 8 | 37.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
6350458 | HPSS 6350458 | 200 | 3 |  | 1549 | 530 | 353 | UNKV |  | 353 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 2005 | 108.1 | 24.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 108.1 |  | 0 | 0
6554531 | HPSS 6414531 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 64 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 64 |  | 0 | 0
6490017 | HPSS 6490017 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 37 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 37 |  | 0 | 0
6490019 | HPSS 6490019 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 28 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 28 |  | 0 | 0
6490021 | HPSS 6490021 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 10 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
6490024 | HPSS 6490024 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 17 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
6490026 | HPSS 6490026 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 42 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
6490027 | HPSS 6490027 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 45 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
6490028 | HPSS 6490028 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 6.1 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6.1 |  | 0 | 0
6490029 | HPSS 6490029 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 14 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
6490032 | HPSS 6490032 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 15 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
6490036 | HPSS 6490036 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 44 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 44 |  | 0 | 0
6490037 | HPSS 6490037 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 10 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
6490040 | HPSS 6490040 | 250 | 3 |  | 1549 | 400 | 266 | UNKV |  | 266 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 55 | 36.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
6490043 | HPSS 6490043 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 38 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
6490051 | HPSS 6490051 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 40.1 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.1 |  | 0 | 0
6490055 | HPSS 6490056 | 250 | 3 |  | 1549 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 40.6 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 40.6 |  | 0 | 0
6490057 | HPSS 6490057 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 9 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
6490058 | HPSS 6490058 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 50 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
6490060 | HPSS 6490060 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 17 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
6490069 | HPSS 6490069 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 49 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49 |  | 0 | 0
6490071 | HPSS 6490071 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 41 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 41 |  | 0 | 0
6491000 | HPSS 6490085 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 87 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 87 |  | 0 | 0
6490091 | HPSS 6490091 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 50 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
6490092 | HPSS 6490092 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 93 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 93 |  | 0 | 0
6490094 | HPSS 6490094 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 16.1 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16.1 |  | 0 | 0
6490095 | HPSS 6490095 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 47 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
6490096 | HPSS 6490096 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2003 | 36 | 25.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
6490097 | HPSS 6490097 | 250 | 3 |  | 1549 | 680 | 453 | UNKV |  | 453 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 35 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
6490120 | HPSS 6490120 | 250 | 3 |  | 933 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1982 | 72 | 44.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 72 |  | 0 | 0
6490121 | HPSS 6490121 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 33 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 33 |  | 0 | 0
6490122 | HPSS 6490122 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2002 | 15 | 26.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 15 |  | 0 | 0
6490123 | HPSS 6490123 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1984 | 96 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 96 |  | 0 | 0
6490127 | HPSS 6490127 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1984 | 86 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 86 |  | 0 | 0
6490151 | HPSS 6490151 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 95 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 95 |  | 0 | 0
6490153 | HPSS 6490153 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 19 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 19 |  | 0 | 0
6490155 | HPSS 6490155 | 250 | 3 |  | 1549 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1982 | 51 | 36.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
6490156 | HPSS 6490156 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 30 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 30 |  | 0 | 0
6490164 | HPSS 6490164 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 18 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18 |  | 0 | 0
6490170 | HPSS 6490170 | 250 | 3 |  | 933 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 2.375 | 0.154 | 24000 | 0.6 | YES | NA | NA | 8.03% | NA | 1982 | 285.1 | 45.53 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 285.1 |  | 0 | 0
6490995 | HPSS 6490995 | 250 | 3 |  | 1549 | 700 | 466 | UNKV |  | 466 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 43.6 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43.6 |  | 0 | 0
6490996 | HPSS 6490996 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 42 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
6491020 | HPSS 6491020 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 12 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
6491970 | HPSS 6491970 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 12.8 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12.8 |  | 0 | 0
6491974 | HPSS 6491974 | 250 | 3 |  | 1193 | 375 | 250 | UNKV |  | 250 | X | Service | UNVALID | 1.315 | 0.109 | 24000 | 0.6 | YES | NA | NA | 6.28% | NA | 1982 | 20 | 42.78 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20 |  | 0 | 0
6491975 | HPSS 6491975 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 4 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 4 |  | 0 | 0
6491977 | HPSS 6491977 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 9 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
6491979 | HPSS 6491979 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 8 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
6492006 | HPSS 6492006 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 8 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
6492090 | HPSS 6492090 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 54 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 54 |  | 0 | 0
6492100 | HPSS 6492100 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 47 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 47 |  | 0 | 0
6492105 | HPSS 6492105 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 9 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 9 |  | 0 | 0
6492106 | HPSS 6492106 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1997 | 21 | 28.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 21 |  | 0 | 0
6492107 | HPSS 6492107 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 13 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
6492110 | HPSS 6492110 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 4.84% | 4.84% | 1990 | 58 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58 |  | 0 | 0
6542825 | HPSS 6542825 | 200 | 3 |  | 1549 | 780 | 520 | UNKV |  | 520 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1979 | 68 | 36.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 68 |  | 0 | 0
6542893 | HPSS 6542893 | 200 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1997 | 12 | 27.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
6543569 | HPSS 6543569 | 200 | 3 |  | 1549 | 830 | 553 | UNKV |  | 553 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 3.87% | NA | 1979 | 159.1 | 37.87 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 159.1 |  | 0 | 0
6543578 | HPSS 6543578 | 200 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | YES | YES | 3.87% | 3.87% | 1972 | 116.4 | 41.37 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 116.4 |  | 0 | 0
6550181 | HPSS 6550181 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 43 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
6550570 | HPSS 6550570 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 13 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 13 |  | 0 | 0
6553806 | HPSS 6553806 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2010 | 2 | 22.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 2 |  | 0 | 0
6553837 | HPSS 6553837 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2008 | 11 | 23.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
6553839 | HPSS 6553839 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2008 | 11 | 23.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
6554102 | HPSS 6554102 | 250 | 3 |  | 1549 | 550 | 366 | UNKV |  | 366 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 136 | 35.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 136 |  | 0 | 0
6554112 | HPSS 6554112 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 72 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 72 |  | 0 | 0
6554121 | HPSS 6554121 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 12 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
Work Order # | Segment Name | Existing MAOP (psig) | Class Location (1,2,3,4) | Uprate (YES/NO) | Design Pressure 192.619 (a) (1) (psig) | Test Pressure (psig) | Test Pressure 192.619 (a) (2) (psig) | Pressure Class Rating (psig) | Hi-5 Pressure (psig) 192.619 (a) (3) | MAOP per 192.619 (psig) | Meets 192.619 | Meets 192.517 | MAOP Designation | Max Outside Diameter, OD1 (inches) | Min Wall Thickness, WT1 (inches) | Min SMYS, SMYS1 (psig) | Min Longitudinal Joint Factor, E1 (E) | Unknown Pressure Rated Fitting (YES/NO) | Fittings w/ Assumed SMYS (YES/NO) | Fittings w/ Assumed Joint Factor (YES/NO) | Max Pipe % SMYS | Max Fitting % SMYS | Install Date (Year) | Pipe Length (Feet) | Total Score | Action Plan | Action Year |  |  |  | 0 |  | 0 | 0
6554200 | HPSS 6554200 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 64 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 64 |  | 0 | 0
6554205 | HPSS 6554205 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 75 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 75 |  | 0 | 0
6554234 | HPSS 6554234 | 250 | 3 |  | 1549 | 450 | 300 | UNKV |  | 300 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2007 | 17 | 23.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 17 |  | 0 | 0
6554515 | HPSS 6554515 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1991 | 50 | 31.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
6554517 | HPSS 6554517 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 27 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 27 |  | 0 | 0
6554518 | HPSS 6554518 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 18.1 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 18.1 |  | 0 | 0
6554520 | HPSS 6554520 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 50 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 50 |  | 0 | 0
6554525 | HPSS 6554525 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 246.1 | 35.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 246.1 |  | 0 | 0
6554526 | HPSS 6554526 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 7 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
6554527 | HPSS 6554527 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 53 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 53 |  | 0 | 0
6554528 | HPSS 6554528 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 7 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
6554529 | HPSS 6554529 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 69.3 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 69.3 |  | 0 | 0
6554532 | HPSS 6554532 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 56.3 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56.3 |  | 0 | 0
6554533 | HPSS 6554533 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 66.7 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 66.7 |  | 0 | 0
6554534 | HPSS 6554534 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1986 | 38 | 34.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 38 |  | 0 | 0
6554535 | HPSS 6554535 | 250 | 3 |  | 1549 | 500 | 333 | UNKV |  | 333 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1985 | 84 | 34.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 84 |  | 0 | 0
6554536 | HPSS 6554536 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 51 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 51 |  | 0 | 0
6554538 | HPSS 6554538 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1987 | 86.2 | 33.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 86.2 |  | 0 | 0
6554539 | HPSS 6554539 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1988 | 5 | 33.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 5 |  | 0 | 0
6554541 | HPSS 6554541 | 250 | 3 |  | 1549 | 750 | 500 | UNKV |  | 500 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 25 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
6554542 | HPSS 6554542 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1990 | 8 | 32.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 8 |  | 0 | 0
6554543 | HPSS 6554543 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1989 | 42 | 32.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
6554544 | HPSS 6554544 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1971 | 31 | 41.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 31 |  | 0 | 0
6554545 | HPSS 6554545 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 39 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 39 |  | 0 | 0
6554546 | HPSS 6554546 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 14 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 14 |  | 0 | 0
6554547 | HPSS 6554547 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 35 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 35 |  | 0 | 0
6554548 | HPSS 6554548 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1992 | 12 | 31.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
6554553 | HPSS 6554553 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1993 | 7 | 30.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 7 |  | 0 | 0
6554557 | HPSS 6554557 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 43 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
6554558 | HPSS 6554558 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 61.4 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 61.4 |  | 0 | 0
6554559 | HPSS 6554559 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 6 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 6 |  | 0 | 0
6554561 | HPSS 6554561 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 45 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
6554562 | HPSS 6554562 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 62 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 62 |  | 0 | 0
6554563 | HPSS 6554563 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1994 | 58.2 | 30.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 58.2 |  | 0 | 0
6554564 | HPSS 6554564 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 55 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 55 |  | 0 | 0
6554565 | HPSS 6554565 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 43 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 43 |  | 0 | 0
6554566 | HPSS 6554566 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 65.8 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 65.8 |  | 0 | 0
6554567 | HPSS 6554567 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 57.4 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 57.4 |  | 0 | 0
6554568 | HPSS 6554568 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1995 | 16 | 29.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 16 |  | 0 | 0
6554569 | HPSS 6554569 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 56.9 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 56.9 |  | 0 | 0
6554575 | HPSS 6554575 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 25 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 25 |  | 0 | 0
6554576 | HPSS 6554576 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 20.5 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 20.5 |  | 0 | 0
6554577 | HPSS 6554577 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 45 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 45 |  | 0 | 0
6554585 | HPSS 6554585 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2004 | 12 | 25.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 12 |  | 0 | 0
6554617 | HPSS 6554617 | 250 | 3 |  | 1549 | 600 | 400 | UNKV |  | 400 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2008 | 60 | 23.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 60 |  | 0 | 0
6554621 | HPSS 6554621 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 10 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 10 |  | 0 | 0
6554622 | HPSS 6554622 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1996 | 27 | 29.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 27 |  | 0 | 0
6554623 | HPSS 6554623 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 65 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 65 |  | 0 | 0
6554631 | HPSS 6554631 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1999 | 36 | 27.84 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 36 |  | 0 | 0
6554635 | HPSS 6554635 | 250 | 3 |  | 1549 | 650 | 433 | UNKV |  | 433 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 2000 | 11 | 27.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 11 |  | 0 | 0
6554705 | HPSS 6554705 | 250 | 3 |  | 1549 | 610 | 406 | UNKV |  | 406 | X | Service | UNVALID | 1.05 | 0.113 | 24000 | 0.6 | YES | NA | NA | 4.84% | NA | 1998 | 22 | 28.34 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 22 |  | 0 | 0
7789599637 | HPSS 7789599637 | 250 | 3 |  | 2260 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2014 | 53 | 14.82 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 53 |  | 0 | 0
8720430548 | HPSS 8720430548 | 250 | 3 |  | 2260 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2015 | 49.6 | 14.32 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 49.6 |  | 0 | 0
9019198110 | HPSS 9019198110 | 250 | 3 |  | 2260 | 800 | 533 | UNKV |  | 533 | X | Service | UNVALID | 1.05 | 0.113 | 35000 | 0.6 | YES | NA | NA | 3.32% | NA | 2013 | 42 | 15.32 | Expose/Verify, DIMP/TIMP | 2018-2028 | 1 | 1 | 0 | 42 |  | 0 | 0
162732 | 020-V-075 | 175 | 3 |  | 877 | 650 | 433 | 250 |  | 250 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.98% | 5.62% | 2009 | 60 | 28.98 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 60 |  | 0 | 0
23706 | 2" South Sunnyside H.P. Line | 200 | 3 |  | 1056 | 750 | 500 | NA |  | 500 | X |  | UNVALID | 6.625 | 0.25 | 35000 | 0.8 | NO | NO | YES | 7.57% | 4.41% | 1975 | 3177.2 | 51.07 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 3177.2 |  | 0 | 0
31613 | 2" South Sunnyside H.P. Line | 200 | 3 |  | 1193 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 4.41% | 5.03% | 1985 | 465.2 | 41.03 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 465.2 |  | 0 | 0
20895 | 2" Sunnyside H.P. Line | 200 | 3 |  | 641 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 3.5 | 0.156 | 24000 | 0.6 | NO | YES | YES | 9.35% | 5.03% | 1972 | 1303.4 | 58.35 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 1303.4 |  | 0 | 0
21157 | 2" Sunnyside H.P. Line | 200 | 3 |  | 1361 | 750 | 500 | NA |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 4.41% | 4.41% | 1973 | 998.9 | 41.41 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 998.9 |  | 0 | 0
29852 | 3” Granger H.P. Line | 175 | 3 |  | 1011 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.8 | NO | YES | YES | 5.98% | 6.92% | 1982 | 94.9 | 43.42 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 94.9 |  | 0 | 0
46712 | 4" Grandview H.P. Line | 250 | 3 |  | 499 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 12.32% | 15.02% | 1994 | 448 | 51.52 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 448 |  | 0 | 0
32388 | 4" Selah H.P. Line | 250 | 3 |  | 1193 | 470 | 313 | 1440 |  | 313 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | YES | YES | 5.51% | 6.28% | 1986 | 18.7 | 40.78 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 18.7 |  | 0 | 0
32731 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1986 | 13.7 | 36.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 13.7 |  | 0 | 0
34191 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 625 | 416 | 1440 |  | 416 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1986 | 160.1 | 37.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 160.1 |  | 0 | 0
35948 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 750 | 500 | 1440 |  | 500 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1988 | 60.9 | 35.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 60.9 |  | 0 | 0
37216 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1989 | 63 | 34.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 63 |  | 0 | 0
46583 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1994 | 81.2 | 32.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 81.2 |  | 0 | 0
P0085306 | 4" Selah H.P. Line | 250 | 3 |  | 1361 | 750 | 500 | 275 |  | 275 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 2008 | 75 | 25.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 75 |  | 0 | 0
44366 | 4" Selah H.P. Line (Inlet 032-R-034) | 250 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 1993 | 64.8 | 32.51 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 64.8 |  | 0 | 0
20819 | 8" Yakima H.P. Line | 200 | 3 |  | 418 | 700 | 466 | 720 |  | 418 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 6.84% | 19.12% | 1972 | 25 | 65.62 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 25 |  | 0 | 0
24188 | 8" Yakima H.P. Line | 200 | 3 |  | 418 | 750 | 500 | 275 |  | 275 | X |  | UNVALID | 8.625 | 0.188 | 35000 | 0.8 | NO | YES | YES | 13.11% | 19.12% | 1978 | 331 | 63.62 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 331 |  | 0 | 0
52943 | 8" Yakima H.P. Line | 200 | 3 |  | 499 | 625 | 416 | 720 |  | 416 | X |  | UNVALID | 8.625 | 0.25 | 35000 | 0.8 | NO | YES | YES | 9.86% | 12.02% | 1997 | 647.2 | 51.02 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 647.2 |  | 0 | 0
42292 | Emerald Rd. Canal Crossing | 200 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 6.84% | 5.42% | 1993 | 61.3 | 33.84 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 61.3 |  | 0 | 0
59550 | Inlet 020-R-054 | 250 | 3 |  | 728 | 750 | 500 | 720 |  | 500 | X |  | UNVALID | 4.5 | 0.156 | 35000 | 0.6 | NO | NO | YES | 10.30% | 10.30% | 2000 | 29.5 | 38.8 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 29.5 |  | 0 | 0
18926 | Inlet 020-R-025 | 175 | 3 |  | 499 | 700 | 466 | 1440 |  | 466 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | YES | YES | 5.98% | 10.52% | 1971 | 24.5 | 57.52 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 24.5 |  | 0 | 0
33288 | Inlet 032-R-001 | 200 | 3 |  | 1361 | 600 | 400 | 1440 |  | 400 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 4.41% | 4.41% | 1985 | 683.6 | 35.41 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 683.6 |  | 0 | 0
P0084568 | Inlet 032-R-022 | 250 | 3 |  | 1361 | 760 | 506 | 1440 |  | 506 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NO | YES | 5.51% | 5.51% | 2008 | 12 | 25.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 12 |  | 0 | 0
41768 | Inlet 032-R-031 | 250 | 3 |  | 1361 | 650 | 433 | 1440 |  | 433 | X |  | UNVALID | 2.375 | 0.154 | 35000 | 0.6 | NO | NA | NA | 5.51% | NA | 1992 | 60 | 33.01 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 60 |  | 0 | 0
47008 | Inlet 032-R-038 | 250 | 3 |  | 877 | 600 | 400 | 720 |  | 400 | X |  | UNVALID | 4.5 | 0.188 | 35000 | 0.6 | NO | NO | YES | 8.55% | 6.78% | 1994 | 133.2 | 36.05 | DIMP/TIMP, Missing 192.517 | 2018-2019 | 1 | 1 | 0 | 133.2 |  | 0 | 0
| "VALID" pipeline segments | [11 empty] | 525 | [5 empty] | "earlier than 1971" |  | Pre-code count |  | 499 | 3164283.3 | Total pipeline feet |  |  | 3176 | 2677 | 1403100 | 1761183.3 | 525 | 484667.3 | 1256145.1 | 35 | 490
| "UNVALID" pipeline segments | [11 empty] | 2651 | [5 empty] | "later than 1970" |  | Post-code count |  | 2677 | [5 empty] | (post-code count)
| total segments | [11 empty] | 3176 | [7 empty] | total segments |  | 3176
Staff's Summary
[28 empty] | Pipeline classification | Feet | Pct of total feet | No. of Segments | Pct of total segments | "Valid" segments | Pct of class segments that are "valid" | "Valid" feet | Pct of class feet that are "valid"
[28 empty] | Pre-code | 1403100 | 44.34% | 499 | 15.71% | 35 | 7.014% | 484667.3 | 34.54%
[28 empty] | Post-code | 1761183.3 | 55.66% | 2677 | 84.29% | 490 | 18.3% | 1256145.1 | 71.32%
[28 empty] | Total | 3164283.3 | 100% | 3176 | 100% | 525 | 16.53% | 1740812.4 | 55.01%
Conclusion: Post-code pipe should all be documented. Staff will not allow 55.7 percent of aggregate
expenses such as documentation audits, based on the overall percentage of pipeline footage, as they
are related to documenting post-code pipe. Staff feels this is being conservative and generous to the
company as a case could be made to disallow 84.3% of these aggregate expenses based on the number of
pipeline segments.
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1

## Pipeline Analysis Summary
Cascade Natural Gas Corporation
Summary of Pipeline Plan Information regarding Pipeline Classification between Pre- and Post-Code Pipe
Pipeline classification | Feet | Pct of total feet | No. of Segments | Pct of total segments | "Valid" segments | Pct of class segments that are "valid" | "Valid" feet | Pct of class feet that are "valid"
Pre-code | 1403100 | 44.34% | 499 | 15.71% | 35 | 1.102% | 484667.3 | 15.32%
Post-code | 1761183.3 | 55.66% | 2677 | 84.29% | 490 | 15.43% | 1256145.1 | 39.7%
Total | 3164283.3 | 100% | 3176 | 100% | 525 | 16.53% | 1740812.4 | 55.01%
Conclusion: Post-code pipe should all be documented. Staff will not allow 55.7 percent of aggregate
expenses such as documentation audits, based on the overall percentage of pipeline footage, as they
are related to documenting post-code pipe. Staff feels this is being conservative and generous to the
company as a case could be made to disallow 84.3% of these aggregate expenses based on the number of
pipeline segments.